## data (hidden)
PASSWORD | WILMARUTILITY2020 | [9 empty] | CELL CALLING | 2
[11 empty] | 1 | RO WATER
[9 empty] | RO & MIXBED |  |  | RO TANK | 100% |  | BARIS 1 | [5 empty] | BARIS 6 |  |  |  | BARIS 11 |  |  |  | BARIS 16 |  |  |  | BARIS 21 |  | cell link grafik | 117
[9 empty] | RO & MMF |  |  | RO XI'AN | 100% |  | CELL LINK | SECTION | CONFORMANCE | [5 empty] | CELL LINK | SECTION | CONFORMANCE |  |  |  | CELL LINK | SECTION | CONFORMANCE
[9 empty] | RAW WATER |  |  | RO YAHUA | 100% |  | 1 | RO TANK | 100% | [5 empty] | 1 | [5 empty] | 1 | [5 empty] | SWRO 2
[9 empty] | FLOW STEAM |  |  | RO JIANGSHU | stop |  | 2 | DEMIN TANK | 83.33% | [5 empty] | 2 | BUFFER DEMIN | 100% |  |  |  | 2
[9 empty] | BOILER & BFW |  | 2 | DEMIN WATER |  |  | 3 | DOMESTIC TANK | 100% | [5 empty] | 3 | RO BRINE #1 | no data |  |  |  | 3 | [6 empty] | FRC In DAF | turbidity | turbidity | turbidity | turbid in mmf | iron out mmf | turbidity out mmf | pH feed | iron | FRC | turbidity | pH Perm a | Cond Perm a | pH Perm b | Cond Perm b
[9 empty] | SWRO |  |  | BUFFER DEMIN | 100% |  | 4 | DEMIN TANK | no data | BOILER PP#1 | 92.86% | 100% | FEED | BOILER | 4 | CONDENSATE MPS BH | 100% | BOILER HP GAS | stop | 100% | 4 |  |  | BOILER HRSG #2 | 100% | stop | SWRO 2 | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
[9 empty] | CHEMICAL CONSUMPT BOILER |  |  | DEMIN TANK | 83.33% |  | 5 | SWRO 1 | stop | [5 empty] | 5 | [5 empty] | 5
[9 empty] | COOLING TOWER |  |  | RO DYNALON 1 | 100% |  | 6 | COOLING TOWER GT 1 | stop | [5 empty] | 6 | [5 empty] | 6
[12 empty] | RO DYNALON 2 | no data
[12 empty] | RO DYNALON #4 | no data |  | BARIS 2 | [28 empty] | performance | problem | root cause | recommendation
[12 empty] | NEW RO | 100% |  | CELL LINK | SECTION | CONFORMANCE |  |  |  | BARIS 7 |  |  |  | BARIS 12 |  |  |  | BARIS 17 | [12 empty] | 1 | FRC In DAF | FRC | 1 | 1 | 1 | [22 empty] | pH feed
[12 empty] | MIXBED | no data |  | 1 | RO XI'AN | 100% |  |  |  | CELL LINK | SECTION | CONFORMANCE |  |  |  | CELL LINK | SECTION | CONFORMANCE | [12 empty] | 2 | turbidity | FRC | 1 | 1 | 1
[5 empty] | 1 | SWRO 1 | stop |  |  |  | 3 | RAW WATER : |  |  | 2 | RO DYNALON 1 | 100% |  |  |  | 1 | [5 empty] | 1 | [14 empty] | 3 | turbidity | turbidity | 2 | 2 | 2
[5 empty] | 2 | SWRO 2 | 86.21% |  |  |  |  | DOMESTIC TANK | 100% |  | 3 | MIXING TANK | 100% |  |  |  | 2 | [5 empty] | 2 | [14 empty] | 4 | turbidity | turbidity | 3 | 3 | 3
[5 empty] | 3 | SWRO 3 | 91.3% |  |  |  |  | MIXING TANK | 100% |  | 4 | CONDENSATE TANK 200 | 75% | BOILER PP#2 | 92.86% | 100% | 3 | RO BRINE #2 | no data |  |  |  | 3 | [14 empty] | 5 | turbid in mmf | turbidity | 1 | 1 | 1
[5 empty] | 4 | SWRO 4 | stop |  |  |  |  | RAW WATER TANK | 100% |  | 5 | SWRO 2 | 86.21% |  |  |  | 4 | CONDENSATE HPS BH | 100% | BOILER MP | no data | stop | 4 |  |  | BOILER OMNICAL | stop | 100% | [9 empty] | 6 | iron out mmf | turbidity inlet mmf | 2 | 2 | 2
[5 empty] | 5 | PRODUCT SWRO | 70% |  |  |  |  | PDAM | 100% |  | 6 | COOLING TOWER GT 2 | stop |  |  |  | 5 | [5 empty] | 5 | [14 empty] | 7 | turbidity out mmf | iron outlet mmf
[5 empty] | 6 | [6 empty] | DYNALON #3 | no data | [7 empty] | 6 | [5 empty] | 6 | [14 empty] | 8 | pH feed | turbidity outlet mmf
[5 empty] | 7 | [6 empty] | RO BRINE #1 | no data |  | BARIS 3 | [26 empty] | 9 | iron | pH feed
[5 empty] | 8 | [6 empty] | RO BRINE #2 | no data |  | CELL LINK | SECTION | CONFORMANCE |  |  |  | BARIS 8 |  |  |  | BARIS 13 |  |  |  | BARIS 18 | [12 empty] | 10 | FRC | iron
[5 empty] | 9 | [5 empty] | 4 | RO BRINE #3 | no data |  | 1 | RO YAHUA | 100% |  |  |  | CELL LINK | SECTION | CONFORMANCE |  |  |  | CELL LINK | SECTION | CONFORMANCE | [12 empty] | 11 | turbidity | FRC
[5 empty] | 10 | [6 empty] | FLOW STEAM : | 100% |  | 2 | RO DYNALON 2 | no data |  |  |  | 1 | [5 empty] | 1 | [14 empty] | 12 | pH Perm a | turbidity
[5 empty] | 11 | [6 empty] | BOILER PP (oC) | 100% |  | 3 | RAW WATER TANK | 100% |  |  |  | 2 | [5 empty] | 2 | [14 empty] | 13 | Cond Perm a | pH perm a
[5 empty] | 12 | [6 empty] | BOILER HP COAL (oC) | 100% |  | 4 | CONDENSATE TURBIN #3 | stop | BOILER PP#3 | 92.86% | 100% | 3 | RO BRINE #3 | no data |  |  |  | 3 | [14 empty] | 14 | pH Perm b | Cond perm a
[5 empty] | 13 | [6 empty] | BOILER HP GAS (oC) | 100% |  | 5 | SWRO 3 | 91.3% |  |  |  | 4 | CONDENSATE MPS GT | 100% | BOILER TOH #3 | stop | stop | 4 | [14 empty] | 15 | Cond Perm b | pH perm b
[5 empty] | 14 | [6 empty] | BOILER MP (oC) | 100% |  | 6 | COOLING TOWER PP | 100% |  |  |  | 5 | [5 empty] | 5 | [14 empty] | 16 |  | Cond perm b
[5 empty] | 15 | [6 empty] | BOILER TOH (oC) | 100% | [7 empty] | 6 | [5 empty] | 6 | [14 empty] | 17
[5 empty] | 16 | [5 empty] | 5 | BOILER HRSG (oC) |  |  | BARIS 4 | [11 empty] | 7 | [14 empty] | 18
[5 empty] | 17 | [6 empty] | BOILER & BFW : |  |  | CELL LINK | SECTION | CONFORMANCE |  |  |  | BARIS 9 |  |  |  | BARIS 14 | [16 empty] | 19
[5 empty] | 18 | [6 empty] | DEMIN TANK | no data |  | 1 | RO JIANGSHU | stop |  |  |  | CELL LINK | SECTION | CONFORMANCE | [5 empty] | BARIS 19 | [12 empty] | 20
[5 empty] | 19 | [6 empty] | CONDENSATE TANK 200 | 75% |  | 2 | RO DYNALON #4 | no data |  |  |  | 1 | [5 empty] | CELL LINK | SECTION | CONFORMANCE | [12 empty] | 21
[5 empty] | 20 | [6 empty] | CONDENSATE TURBIN #3 | stop |  | 3 | PDAM | 100% |  |  |  | 2 | [5 empty] | 1 | [14 empty] | 22
[5 empty] | 21 | [6 empty] | CONDENSATE MPS PP | stop |  | 4 | CONDENSATE MPS PP | stop | BOILER PP#4 | 92.86% | stop | 3 | [5 empty] | 2 | [14 empty] | 23
[5 empty] | 22 | [6 empty] | CONDENSATE LPS PP | 100% |  | 5 | SWRO 4 | stop |  |  |  | 4 |  |  | BOILER TOH #4 | stop | stop | 3 | [14 empty] | 24
|  |  | Cell Calling | 5 | 23 | [6 empty] | CONDENSATE MPS BH | 100% |  | 6 | COOLING TOWER COMPRESSOR | 100% |  |  |  | 5 | [5 empty] | 4 | [14 empty] | 25
|  | 1 | RO WATER |  | 24 | [6 empty] | CONDENSATE HPS BH | 100% | [7 empty] | 6 | [5 empty] | 5
|  | 2 | RO DEMIN |  | 25 | [6 empty] | CONDENSATE MPS GT | 100% |  | BARIS 5 | [11 empty] | 6
|  | 3 | RAW WATER |  | 26 | [6 empty] | BFW PP | 92.86% |  | CELL LINK | SECTION | CONFORMANCE |  |  |  | BARIS 10 |  |  |  | BARIS 15 |  | 7
|  | 4 | BOILER & BFW |  | 27 | [6 empty] | BFW HP COAL | stop |  | 1 | [5 empty] | CELL LINK | SECTION | CONFORMANCE
|  | 5 | SWRO | [8 empty] | BFW HP GAS | stop |  | 2 | NEW RO | 100% |  |  |  | 1 | [7 empty] | BARIS 20
|  | 6 | COOLING TOWER | [8 empty] | BFW MP | no data |  | 3 | DYNALON #3 | no data |  |  |  | 2 | [5 empty] | CELL LINK | SECTION | CONFORMANCE
|  | 7 | [9 empty] | BFW TOH | stop |  | 4 | CONDENSATE LPS PP | 100% | BOILER HP COAL | stop | 100% | 3 | [5 empty] | 1
[12 empty] | BFW HRSG | 100% |  | 5 | PRODUCT SWRO | 70% |  |  |  | 4 |  |  | BOILER HRSG #1 | 100% | stop | 2
[12 empty] | BFW OMNICAL | stop |  | 6 | COOLING TOWER BOILER HOUSE | no data |  |  |  | 5 | [5 empty] | 3
[12 empty] | BOILER PP#1 | 100% | [7 empty] | 6 | [5 empty] | 4
[12 empty] | BOILER PP#2 | 100% | [13 empty] | 5
[12 empty] | BOILER PP#3 | 100% |  | BFW & BOILER | [11 empty] | 6
[12 empty] | BOILER PP#4 | stop |  | CELL LINK | SECTION | CONFORMANCE | [9 empty] | 7
| 30 | [10 empty] | BOILER HP COAL | 100% |  | 1 | BFW PP
| 2026-09-01 | [10 empty] | BOILER HP GAS | 100% |  | 2 | BFW HP COAL | 100% | [26 empty] | CONTROL | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
| 2026-09-02 | [10 empty] | BOILER MP | stop |  | 3 | BFW HP GAS | 75% | [26 empty] | parameter RO | 1: pH; 2: Conductivity; 3: Total Hardness; 4: Silica; 5: Iron; 6: Chloride
| 2026-09-03 | [10 empty] | BOILER TOH #3 | stop |  | 4 | BFW MP | stop | [25 empty] | 1 | RO TANK | 1: good control; 2: good control; 3: good control; 4: good control; 5: good control; 6: good control
| 2026-09-04 | [10 empty] | BOILER TOH #4 | stop |  | 5 | BFW TOH | stop | [25 empty] | 2 | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| 2026-09-05 | [10 empty] | BOILER HRSG #1 | stop |  | 6 | BFW HRSG | 0% | [25 empty] | 3 | parameter xi'an | inlet FRC | pH Feed a | Conduct feed a | FRC feed a | Turbidity feed a | pH Feed b | Conduct feed b | FRC feed b | turbidity feed b | pH permeate a | conduct permeate a | silica permeate a | pH permeate b | conduct permeate b | silica permeate b | pH mix a | conduct mix a | hard mix a | silica mix a | iron mix a | pH mix b | conduct mix b | hard mix b | silica mix b | iron mix b
| 2026-09-06 | [10 empty] | BOILER HRSG #2 | stop |  | 7 | BFW OMNICAL | 0% | [25 empty] | 4 | RO XI'AN | good control | good control | good control | good control | good control | good control | good control | good control | good control | good control | good control | no data | good control | good control | good control | bad control | bad control | bad control | bad control | bad control | bad control | bad control | bad control | bad control | bad control
| 2026-09-07 | [9 empty] | 6 | BOILER OMNICAL | 100% |  |  | BOILER PP#1 | [26 empty] | 5 | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| 2026-09-08 | [10 empty] | SWRO : |  |  |  | BOILER PP#2 | [26 empty] | 6 | parameter yahua | inlet FRC | pH Feed | Conduct feed | FRC feed | Turbidity feed | pH permeate | conduct permeate | silica permeate | pH mix a | conduct mix a | hard mix a | silica mix a | iron mix a | pH mix b | conduct mix b | hard mix b | silica mix b | iron mix b
| 2026-09-09 | [10 empty] | SWRO 1 | stop |  |  | BOILER PP#3 | [26 empty] | 7 | RO YAHUA | good control | good control | good control | good control | good control | good control | good control | no data | bad control | bad control | bad control | bad control | bad control | bad control | bad control | bad control | bad control | bad control
| 2026-09-10 | [10 empty] | SWRO 2 | 86.21% |  |  | BOILER PP#4 | [26 empty] | 8 | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| 2026-09-11 | [10 empty] | SWRO 3 | 91.3% |  |  | BOILER HP COAL | [26 empty] | 9 | parameter jiangshu | inlet FRC | pH Feed a | Conduct feed a | FRC feed a | Turbidity feed a | pH Feed b | Conduct feed b | FRC feed b | turbidity feed b | pH permeate a | conduct permeate a | silica permeate a | pH permeate b | conduct permeate b | silica permeate b | pH mix a | conduct mix a | hard mix a | silica mix a | iron mix a | pH mix b | conduct mix b | hard mix b | silica mix b | iron mix b
| 2026-09-12 | [10 empty] | SWRO 4 | stop |  |  | BOILER HP GAS | [26 empty] | 10 | RO JIANGSHU | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | bad control | bad control | bad control | bad control | bad control | bad control | bad control | bad control | bad control | bad control
| 2026-09-13 | [9 empty] | 7 | PRODUCT SWRO | 70% |  |  | BOILER MP
| 2026-09-14 | [10 empty] | COOLING TOWER : |  |  |  | BOILER TOH #3 | [26 empty] | 0: Parameter Buffer Demin Tank; 1: pH; 1: Conductivity; 2: Total Hardness; 3: Silica; 4: Iron
| 2026-09-15 | [10 empty] | COOLING TOWER GT 1 | stop |  |  | BOILER TOH #4 | [26 empty] | 8: 11; 0: BUFFER DEMIN; 1: good control; 1: good control; 2: no data; 3: good control; 4: no data
| 2026-09-16 | [10 empty] | COOLING TOWER GT 2 | stop |  |  | BOILER HRSG #1 | [26 empty] | 8: 12; 0: Parameter Demin Tank; 1: pH; 1: Conductivity; 2: Total Hardness; 3: Silica; 4: Iron
| 2026-09-17 | [10 empty] | COOLING TOWER PP | 100% |  |  | BOILER HRSG #2 | [26 empty] | 8: 13; 0: DEMIN TANK; 1: good control; 1: good control; 2: good control; 3: bad control; 4: good control
| 2026-09-18 | [10 empty] | COOLING TOWER COMPRESSOR | 100% |  |  | BOILER OMNICAL | [26 empty] | 8: 14; 0: 0; 1: 1; 1: 1; 2: 2; 3: 3; 4: 4; 1: 1; 2: 2; 3: 3
| 2026-09-19 | [10 empty] | COOLING TOWER BOILER HOUSE | no data | [29 empty] | 8: 15; 0: parameter dyn 1; 1: inlet FRC; 1: pH Feed; 2: Conduct feed; 3: FRC feed; 4: turbidity feed; 1: pH permeate; 2: conduct permeate; 3: silica permeate
| 2026-09-20 | [41 empty] | 8: 16; 0: RO DYNALON 1; 1: good control; 1: good control; 2: good control; 3: good control; 4: good control; 1: good control; 2: good control; 3: good control
| 2026-09-21 | [41 empty] | 8: 17; 0: 0; 1: 1; 1: 1; 2: 2; 3: 3; 4: 4; 1: 1; 2: 2; 3: 3
| 2026-09-22 | [41 empty] | 8: 18; 0: parameter dyn 2; 1: inlet FRC; 1: pH Feed; 2: Conduct feed; 3: FRC feed; 4: turbidity feed; 1: pH permeate; 2: conduct permeate; 3: silica permeate
| 2026-09-23 | [41 empty] | 8: 19; 0: RO DYNALON 2; 1: good control; 1: good control; 2: good control; 3: good control; 4: good control; 1: #NAME?; 2: #NAME?; 3: #NAME?
| 2026-09-24 | [41 empty] | 20 | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 1 | 2 | 3 | 4 | 5
| 2026-09-25 | [41 empty] | 21 | parameter dyn 4 | inlet FRC | pH Feed | Conduct feed | FRC feed | turbidity feed | pH permeate | conduct permeate | silica permeate | pH mix | conduct mix | hard mix | silica mix | iron mix
| 2026-09-26 | [41 empty] | 22 | RO DYNALON #4 | good control | good control | good control | good control | good control | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
| 2026-09-27 | [41 empty] | 23 | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3
| 2026-09-28 | [41 empty] | 24 | parameter new ro | inlet FRC | pH Feed | Conduct feed | FRC feed | turbidity feed | pH permeate | conduct permeate | silica permeate
| 2026-09-29 | [41 empty] | 25 | NEW RO | stop | stop | stop | stop | stop | #NAME? | #NAME? | #NAME?
| 2026-09-30 | [41 empty] | 20: 26; 0: 0; 1: 1; 1: 2; 2: 3
| 2026-10-01 | [41 empty] | 20: 27; 0: parameter domestic; 1: pH; 1: Conduct; 2: T.Hardness
| Conformance | [41 empty] | 20: 28; 0: DOMESTIC TANK; 1: good control; 1: good control; 2: good control
[43 empty] | 29 | parameter mixing | pH | Conduct | T.Hardness
[43 empty] | 30 | MIXING TANK | good control | good control | good control
[43 empty] | 31 | parameter raw water | pH | Conduct | T.Hardness
| #REF! | [41 empty] | 20: 32; 0: RAW WATER TANK; 1: good control; 1: good control; 2: good control
| OVERALL VALUE | [41 empty] | 20: 33; 0: parameter raw water; 1: pH; 1: Conduct; 2: T.Hardness
| Date | [41 empty] | 20: 34; 0: PDAM; 1: good control; 1: good control; 2: good control
[43 empty] | 35 | 0 | 1 | 1 | 1 | 1 | 2
[43 empty] | 36 | parameter dyn 3 | FRC after biocide | FRC after 7408 | pH Feed | pH permeate | conduct permeate
[43 empty] | 37 | DYNALON #3 | no data | no data | no data | no data | no data
| 30 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | [34 empty] | 20: 38; 0: parameteer brine 1; 1: FRC after biocide; 1: FRC after 7408; 2: pH Feed; 3: pH permeate; 4: conduct permeate
| Date | RO WATER | RO DEMIN | RAW WATER | FLOW STEAM | BOILER & BFW | SWRO | COOLING TOWER |  | Date | RO WATER | RO DEMIN | RAW WATER | BOILER & BFW | SWRO | COOLING TOWER |  |  |  | AVERAGE DAILY COMPLIANCE |  | MTD | MTD COMPLIANCE | [19 empty] | 20: 39; 0: RO BRINE #1; 1: no data; 1: no data; 2: no data; 3: no data; 4: no data
1 | 2026-09-01 | 100% | 100% | 98.04% | 100% | 99.21% | 88.5% | 100% |  | 2026-09-01 | 100% | 100% | 98.04% | 99.21% | 88.5% | 100% |  |  |  | 97.62% |  | 97.62% | 97.62% | [19 empty] | 20: 40; 0: parameter brine 2; 1: FRC after biocide; 1: FRC after 7408; 2: pH Feed; 3: pH permeate; 4: conduct permeate
2 | 2026-09-02 | 100% | 100% | 99.02% | 100% | 98.41% | 87.89% | 100% |  | 2026-09-02 | 100% | 100% | 99.02% | 98.41% | 87.89% | 100% |  |  |  | 97.55% |  | 97.59% | 97.59% | [19 empty] | 20: 41; 0: RO BRINE #2; 1: no data; 1: no data; 2: no data; 3: no data; 4: no data
3 | 2026-09-03 | 100% | 100% | 99.02% | 100% | 99.8% | 92.29% | 100% |  | 2026-09-03 | 100% | 100% | 99.02% | 99.8% | 92.29% | 100% |  |  |  | 98.52% |  | 97.9% | 97.9% | [19 empty] | 20: 42; 0: parameter brine 3; 1: FRC after biocide; 1: FRC after 7408; 2: pH Feed; 3: pH permeate; 4: conduct permeate
4 | 2026-09-04 | 100% | 100% | 98.04% | 100% | 99.62% | 89.79% | 100% |  | 2026-09-04 | 100% | 100% | 98.04% | 99.62% | 89.79% | 100% |  |  |  | 97.91% |  | 97.9% | 97.9% | [19 empty] | 20: 43; 0: RO Brine #3; 1: no data; 1: no data; 2: no data; 3: no data; 4: no data
5 | 2026-09-05 | 100% | 100% | 100% | 100% | 98.97% | 94.91% | 100% |  | 2026-09-05 | 100% | 100% | 100% | 98.97% | 94.91% | 100% |  |  |  | 98.98% |  | 98.12% | 98.12% | [19 empty] | 20: 44; 0: 0; 1: 1; 1: 2; 2: 3; 3: 4; 4: 5
6 | 2026-09-06 | 100% | 100% |  | 100% | 90.54% |  |  |  | 2026-09-06 | 100% | 100% |  | 90.54% | [5 empty] | 96.85% |  | 97.91% | 97.91% | [19 empty] | 20: 45; 0: parameter demin tank; 1: pH; 1: Conductivity; 2: Total Hardness; 3: Silica; 4: Iron
7 | 2026-09-07 | 100% | 100% | 100% | 100% | 98.4% | 90.46% | 100% |  | 2026-09-07 | 100% | 100% | 100% | 98.4% | 90.46% | 100% |  |  |  | 98.14% |  | 97.94% | 97.94% | [19 empty] | 20: 46; 0: DEMIN TANK; 1: no data; 1: no data; 2: no data; 3: no data; 4: no data
8 | 2026-09-08 | 100% | 100% | 98.82% | 100% | 99.15% | 89.79% | 100% |  | 2026-09-08 | 100% | 100% | 98.82% | 99.15% | 89.79% | 100% |  |  |  | 97.96% |  | 97.94% | 97.94% | [19 empty] | 20: 47; 0: parameter condensate; 1: pH; 1: Conductivity; 2: Total Hardness; 3: Silica; 4: Iron
9 | 2026-09-09 | 100% | 100% | 98.82% | 100% | 95.68% | 89.79% | 100% |  | 2026-09-09 | 100% | 100% | 98.82% | 95.68% | 89.79% | 100% |  |  |  | 97.38% |  | 97.88% | 97.88% | [19 empty] | 20: 48; 0: CONDENSATE TANK 200; 1: bad control; 1: good control; 2: good control; 3: good control; 4: #REF!
10 | 2026-09-10 | 100% | 100% | 98.82% | 100% | 99.76% | 89.79% | 100% |  | 2026-09-10 | 100% | 100% | 98.82% | 99.76% | 89.79% | 100% |  |  |  | 98.06% |  | 97.9% | 97.9% | [19 empty] | 20: 49; 0: 0; 1: 1; 1: 2; 2: 3
11 | 2026-09-11 | 100% | 100% | 100% | 100% | 99.52% | 89.79% | 100% |  | 2026-09-11 | 100% | 100% | 100% | 99.52% | 89.79% | 100% |  |  |  | 98.22% |  | 97.93% | 97.93% | [19 empty] | 20: 50; 0: parameter steam; 1: pH; 1: Conductivity; 2: Silica
12 | 2026-09-12 | 100% | 100% | 98.82% | 100% | 99.29% | 89.79% | 100% |  | 2026-09-12 | 100% | 100% | 98.82% | 99.29% | 89.79% | 100% |  |  |  | 97.98% |  | 97.93% | 97.93% | [19 empty] | 20: 51; 0: CONDENSATE TURBIN #3; 1: good control; 1: good control; 2: good control
13 | 2026-09-13 | 100% | 100% |  | 100% | 96.85% |  |  |  | 2026-09-13 | 100% | 100% |  | 96.85% | [5 empty] | 98.95% |  | 98.01% | 98.01% | [19 empty] | 20: 52; 0: parameter steam; 1: pH; 1: Conductivity
14 | 2026-09-14 | 100% | 100% | 98.82% | 100% | 97.83% | 95.55% | 100% |  | 2026-09-14 | 100% | 100% | 98.82% | 97.83% | 95.55% | 100% |  |  |  | 98.7% |  | 98.06% | 98.06% | [19 empty] | 20: 53; 0: CONDENSATE MPS PP; 1: good control; 1: good control
15 | 2026-09-15 | 100% | 100% | 98.82% | 100% | 99.79% | 90.88% | 100% |  | 2026-09-15 | 100% | 100% | 98.82% | 99.79% | 90.88% | 100% |  |  |  | 98.25% |  | 98.07% | 98.07% | [19 empty] | 20: 54; 0: parameter steam; 1: pH; 1: Conductivity
16 | 2026-09-16 | 98.61% | 100% | 98.82% | 100% | 92.89% | 89.6% | 100% |  | 2026-09-16 | 98.61% | 100% | 98.82% | 92.89% | 89.6% | 100% |  |  |  | 96.65% |  | 97.98% | 97.98% | [19 empty] | 20: 55; 0: CONDENSATE LPS PP; 1: good control; 1: good control
17 | 2026-09-17 | 84.48% | 98.18% | 98.82% | 100% | 88.27% | 90.78% | 100% |  | 2026-09-17 | 84.48% | 98.18% | 98.82% | 88.27% | 90.78% | 100% |  |  |  | 93.42% |  | 97.72% | 97.72% | [19 empty] | 20: 56; 0: parameter steam; 1: pH; 1: Conductivity
18 | 2026-09-18 | 94.72% | 100% | 98.82% | 100% | 100% | 95.55% | 100% |  | 2026-09-18 | 94.72% | 100% | 98.82% | 100% | 95.55% | 100% |  |  |  | 98.18% |  | 97.74% | 97.74% | [19 empty] | 20: 57; 0: CONDENSATE MPS BH; 1: stop; 1: stop
19 | 2026-09-19 | 100% | 100% | 98.82% | 100% | 94.89% | 90.18% | 100% |  | 2026-09-19 | 100% | 100% | 98.82% | 94.89% | 90.18% | 100% |  |  |  | 97.32% |  | 97.72% | 97.72% | [19 empty] | 20: 58; 0: parameter steam; 1: pH; 1: Conductivity
20 | 2026-09-20 | 85.71% | 100% |  | 100% | 96.85% |  |  |  | 2026-09-20 | 85.71% | 100% |  | 96.85% | [5 empty] | 94.19% |  | 97.54% | 97.54% | [19 empty] | 20: 59; 0: CONDENSATE HPS BH; 1: stop; 1: stop
21 | 2026-09-21 | 100% | 98.18% | 98.82% | 100% | 91.26% | 90.46% | 100% |  | 2026-09-21 | 100% | 98.18% | 98.82% | 91.26% | 90.46% | 100% |  |  |  | 96.46% |  | 97.49% | 97.49% | [19 empty] | 20: 60; 0: parameter steam; 1: pH; 1: Conductivity
22 | 2026-09-22 | 100% | 100% | 98.82% | 100% | 98.11% | 91.33% | 93.75% |  | 2026-09-22 | 100% | 100% | 98.82% | 98.11% | 91.33% | 93.75% |  |  |  | 97% |  | 97.47% | 97.47% | [19 empty] | 20: 61; 0: CONDENSATE MPS GT; 1: stop; 1: stop
23 | 2026-09-23 | 75.87% | 96.82% | 95.97% | 100% | 99.33% | 92.19% | 87.3% |  | 2026-09-23 | 75.87% | 96.82% | 95.97% | 99.33% | 92.19% | 87.3% |  |  |  | 91.25% |  | 97.2% | 97.2% | [19 empty] | 20: 62; 0: 0
24 | 2026-09-24 | 98.15% | 100% | 98.82% | 100% | 99.78% | 91.23% | 100% |  | 2026-09-24 | 98.15% | 100% | 98.82% | 99.78% | 91.23% | 100% |  |  |  | 98% |  | 97.23% | 97.23% | [19 empty] | 20: 63; 0: parameter MIXBED #1
25 | 2026-09-25 | 100% | 100% | 98.82% | 100% | 99.78% | 90.65% | 100% |  | 2026-09-25 | 100% | 100% | 98.82% | 99.78% | 90.65% | 100% |  |  |  | 98.21% |  | 97.27% | 97.27% | [19 empty] | 20: 64; 0: MIXBED #1
26 | 2026-09-26 | 97.73% | 100% | 98.82% | 100% | 95.76% | 93.15% | 100% |  | 2026-09-26 | 97.73% | 100% | 98.82% | 95.76% | 93.15% | 100% |  |  |  | 97.58% |  | 97.28% | 97.28% | [19 empty] | 20: 65; 0: parameter MIXBED #2
27 | 2026-09-27 | 100% | 100% |  | 100% | 99.76% |  |  |  | 2026-09-27 | 100% | 100% |  | 99.76% | [5 empty] | 99.92% |  | 97.38% | 97.38% | [19 empty] | 20: 66; 0: MIXBED #2
28 | 2026-09-28 | 100% | 100% | 98.82% | 100% | 94.21% | 87.62% | 100% |  | 2026-09-28 | 100% | 100% | 98.82% | 94.21% | 87.62% | 100% |  |  |  | 96.78% |  | 97.36% | 97.36% | [19 empty] | 20: 67; 0: parameter MIXBED #3
29 | 2026-09-29 | 100% | 100% | 95.6% | 100% | 98.1% | 89.38% | 100% |  | 2026-09-29 | 100% | 100% | 95.6% | 98.1% | 89.38% | 100% |  |  |  | 97.18% |  | 97.35% | 97.35% | [19 empty] | 20: 68; 0: MIXBED #3
30 | 2026-09-30 | 100% | 97.22% | 100% | 100% | 97.7% | 82.5% | 100% |  | 2026-09-30 | 100% | 97.22% | 100% | 97.7% | 82.5% | 100% |  |  |  | 96.24% |  | 97.31% | 97.31% | [19 empty] | 20: 69; 0: parameter MIXBED #4
31 | 2026-10-01 | [8 empty] | 2026-10-01 | [11 empty] | 97.31% | [20 empty] | 20: 70; 0: MIXBED #4
[11 empty] | 97.84% | [31 empty] | 20: 71; 0: 0
[43 empty] | 72 | 0
[43 empty] | 73 | 0
|  | RO WATER | RO DEMIN | RAW WATER | BOILER & BFW | SWRO | COOLING TOWER | AVE | [34 empty] | 20: 74; 0: 0
| Daily Compliance | 100% | 97.22% | 100% | 97.7% | 82.5% | 100% | 96.24% | [34 empty] | 20: 75; 0: 0
| MTD Compliance | 97.84% | 99.68% | 98.73% | 97.32% | 90.53% | 99.27% | 97.23% | [34 empty] | 20: 76; 0: 0
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | [16 empty] | 77 | 0
| Koreksi : VLOOKUP -> INDEX | 1 | 2 | 3 | 4 | 5 | 6 | [35 empty] | 78 | 0
| parameter RO | pH | Conduct | T. Hardness | Silica | Iron | Chloride | [35 empty] | 79 | 0
| RO TANK | 100% | 100% | 100% | 100% | 100% | 100% | [35 empty] | 80 | 0
|  | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 5 | 6 | [26 empty] | 81 | 0
| parameter xi'an | in FRC | pH Feed a | Conduct feed a | FRC feed a | Turbid feed a | pH Feed b | Conduct feed b | FRC feed b | turbidity feed b | pH permeate a | conduct permeate a | silica permeate a | pH permeate b | conduct permeate b | silica permeate b | [26 empty] | 82 | 0
| RO XI'AN | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | [26 empty] | 83 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 2 | 3 | 4
|  | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | [33 empty] | 84 | parameter boiler high pressure | pH | Conductivity | T. Hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate
| parameter yahua | in FRC | pH Feed | Conduct feed | FRC feed | Turbid feed | pH permeate | conduct permeate | silica permeate | [33 empty] | 85 | BOILER PP#1 | good control | good control | good control | good control | good control | good control | good control | good control | good control | good control
| RO YAHUA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | [33 empty] | 86 | parameter boiler high pressure | pH | Conductivity | T. Hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate
|  | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 5 | 6 | [26 empty] | 87 | BOILER PP#2 | good control | good control | good control | good control | good control | good control | good control | good control | good control | good control
| parameter jiangshu | in FRC | pH Feed a | Conduct feed a | FRC feed a | Turbid feed a | pH Feed b | Conduct feed b | FRC feed b | turbidity feed b | pH permeate a | conduct permeate a | silica permeate a | pH permeate b | conduct permeate b | silica permeate b | [26 empty] | 88 | parameter boiler high pressure | pH | Conductivity | T. Hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate
| RO JIANGSHU | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | [26 empty] | 89 | BOILER PP#3 | good control | good control | good control | good control | good control | good control | stop | stop | stop | stop
[43 empty] | 90 | parameter boiler high pressure | pH | Conductivity | T. Hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate
|  | 1: 1; 1: 2; 2: 3; 3: 4; 4: 5 | [26 empty] | 91 | BOILER PP#4 | good control | good control | good control | good control | good control | good control | good control | good control | good control | good control
| Parameter Buffer Demin Tank | 1: pH; 1: Conductivity; 2: Total Hardness; 3: silica; 4: iron | [26 empty] | 92 | parameter boiler high pressure | pH | Conductivity | T. Hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate
| BUFFER DEMIN | 1: 100%; 1: 100%; 2: no data; 3: 100%; 4: no data | [26 empty] | 93 | BOILER HP COAL | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
| Parameter Demin Tank | 1: pH; 1: Conductivity; 2: Total Hardness; 3: silica; 4: iron | [26 empty] | 94 | parameter boiler high pressure | pH | Conductivity | T. Hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate
| DEMIN TANK | 1: 100%; 1: 100%; 2: 100%; 3: 0%; 4: 100% | [26 empty] | 95 | BOILER HP GAS | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
|  | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | [33 empty] | 96 | 0 | 1 | 2 | 3 | 4 | 5 | 1 | 2 | 3 | 4 | 5 | 6
| parameter dyn 1 | in FRC | pH Feed | Conduct feed | FRC feed | Turbid feed | pH permeate | conduct permeate | silica permeate | [33 empty] | 97 | parameter low pressure | pH | Conductivity | T. Hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite
| RO DYNALON 1 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | [33 empty] | 98 | BOILER MP | stop | stop | no data | stop | stop | stop | stop | stop | stop | stop | stop
|  | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | [33 empty] | 99 | parameter low pressure | pH | Conductivity | T. Hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite
| parameter dyn 2 | in FRC | pH Feed | Conduct feed | FRC feed | Turbid feed | pH permeate | conduct permeate | silica permeate | [33 empty] | 100 | BOILER TOH #3 | good control | good control | good control | good control | good control | stop | stop | stop | stop | stop | stop
| RO DYNALON 2 | 100% | 100% | 100% | 100% | 100% | #NAME? | #NAME? | #NAME? | [33 empty] | 101 | parameter low pressure | pH | Conductivity | T. Hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite
|  | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 1 | 2 | 3 | 4 | 5 | [28 empty] | 102 | BOILER TOH #4 | good control | good control | good control | good control | good control | good control | good control | good control | good control | good control | good control
| parameter dyn 4 | in FRC | pH Feed | Conduct feed | FRC feed | Turbid feed | pH permeate | conduct permeate | silica permeate | pH mix | conduct mix | hard mix | silica mix | iron mix | [28 empty] | 103 | parameter low pressure | pH | Conductivity | T. Hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite
| RO DYNALON #4 | 100% | 100% | 100% | 100% | 100% | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | [28 empty] | 104 | BOILER HRSG #1 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
|  | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | [33 empty] | 105 | parameter low pressure | pH | Conductivity | T. Hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite
| parameter new ro | in FRC | pH Feed | Conduct feed | FRC feed | Turbid feed | pH permeate | conduct permeate | silica permeate | [33 empty] | 106 | BOILER HRSG #2 | stop | stop | stop | stop | no data | stop | stop | stop | stop | stop | stop
| NEW RO | stop | stop | stop | stop | stop | #NAME? | #NAME? | #NAME? | [33 empty] | 107 | parameter low pressure | pH | Conductivity | T. Hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite
|  | 1: 1; 1: 2; 2: 3 | [33 empty] | 108 | BOILER OMNICAL | good control | good control | good control | good control | no data | good control | good control | good control | good control | good control | good control
| parameter domestic | 1: pH; 1: Conduct; 2: T.Hardness | [33 empty] | 109 | 0 | 1 | 1 | 2 | 3 | 1 | 1 | 2 | 1 | 1 | 2 | 3 | 1 | 2 | 1 | 2
| DOMESTIC TANK | 1: 100%; 1: 100%; 2: 100% | [33 empty] | 110 | parameter sea water 1 | FRC | FRC | turbidity | turbidity | turbidity inlet mmf | iron outlet mmf | turbidity outlet mmf | pH feed | iron | FRC | turbidity | pH perm a | Cond perm a | pH perm b | Cond perm b
| parameter mixing | 1: pH; 1: Conduct; 2: T.Hardness | [33 empty] | 111 | SWRO 1 | stop | good control | good control | good control | good control | good control | good control | good control | good control | good control | good control | good control | stop | stop | bad control
| MIXING TANK | 1: 100%; 1: 100%; 2: 100% | [33 empty] | 112 | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 1 | 2 | 1 | 1 | 2 | 3 | 1 | 2 | 1 | 2
| parameter raw water | 1: pH; 1: Conduct; 2: T.Hardness | [33 empty] | 113 | parameter swro 2 | FRC | FRC | turbidity | turbidity | turbidity | turbidity inlet mmf | iron outlet mmf | turbidity outlet mmf | pH feed | iron | FRC | turbidity | pH perm a | Cond perm a | pH perm b | Cond perm b
| RAW WATER TANK | 1: 100%; 1: 100%; 2: 100% | [33 empty] | 114 | SWRO 2 | good control | bad control | bad control | bad control | bad control | good control | good control | good control | good control | good control | good control | good control | good control | good control | good control | bad control
| parameter raw water | 1: pH; 1: Conduct; 2: T.Hardness | [33 empty] | 115 | parameter swro 3 | FRC | FRC | turbidity | turbidity | turbidity | turbidity inlet mmf | iron outlet mmf | turbidity outlet mmf | pH feed | iron | FRC | turbidity | pH perm a | Cond perm a | pH perm b | Cond perm b
| PDAM | 1: 100%; 1: 100%; 2: 100% | [33 empty] | 116 | SWRO 3 | good control | #REF! | good control | good control | good control | bad control | good control | good control | good control | good control | good control | good control | stop | stop | good control | bad control
|  | 1 | 1 | 1 | 1 | 2 | [36 empty] | 117 | 0 | 1 | 1 | 2 | 3 | 1 | 2
| parameter dyn 3 | FRC after biocide | FRC after 7408 | pH Feed | pH permeate | conduct permeate | [36 empty] | 118 | parameter swro 4 | pH feed | iron | FRC | turbidity | pH mix a | Cond mix a
| DYNALON #3 | no data | no data | no data | no data | no data | [36 empty] | 119 | SWRO 4 | stop | stop | stop | stop | stop | stop
| parameteer brine 1 | FRC after biocide | FRC after 7408 | pH Feed | pH permeate | conduct permeate | [36 empty] | 120 | 0 | 1 | 2 | 1 | 2
| RO BRINE #1 | no data | no data | no data | no data | no data | [36 empty] | 121 | parameter product swro | pH pro 1 | Cond pro 1 | pH pro 234 | Cond pro 234
| parameter brine 2 | FRC after biocide | FRC after 7408 | pH Feed | pH permeate | conduct permeate | [36 empty] | 122 | PRODUCT SWRO | good control | bad control | good control | bad control
| RO BRINE #2 | no data | no data | no data | no data | no data | [36 empty] | 123 | 0 | 1 | 2 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
| parameter brine 3 | FRC after biocide | FRC after 7408 | pH Feed | pH permeate | conduct permeate | [36 empty] | 124 | parameter cooling tower | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | Zinc | Orthophosphate (filter) | Free Chlorine | Active Polymer | Aluminium | Chloride | Turbidity | TAB
| RO Brine #3 | no data | no data | no data | no data | no data | [36 empty] | 125 | COOLING TOWER GT 1 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | bad control | bad control | bad control | bad control
|  | 1 | 2 | 3 | 4 | 5 | [36 empty] | 126 | parameter cooling tower | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | Zinc | Orthophosphate (filter) | Free Chlorine | Active Polymer | Aluminium | Chloride | Turbidity | TAB
| parameter demin tank | pH | Conductivity | Total Hardness | Silica | Iron | [36 empty] | 127 | COOLING TOWER GT 2 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | bad control | bad control | bad control | bad control
| DEMIN TANK | no data | no data | no data | no data | no data | [36 empty] | 128 | parameter cooling tower | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | Zinc | Orthophosphate (filter) | Free Chlorine | Active Polymer | Aluminium | Chloride | Turbidity | TAB
| parameter condensate | pH | Conductivity | Total Hardness | Silica | Iron | [36 empty] | 129 | COOLING TOWER PP | good control | good control | good control | good control | no data | good control | no data | good control | good control | good control | good control | bad control | bad control | bad control | bad control
| CONDENSATE TANK 200 | 0% | 100% | 100% | 100% | #REF! | [36 empty] | 130 | parameter cooling tower | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | Zinc | Orthophosphate (filter) | Free Chlorine | Active Polymer | Aluminium | Chloride | Turbidity | TAB
|  | 1 | 2 | 3 | [38 empty] | 131 | COOLING TOWER COMPRESSOR | good control | good control | good control | good control | no data | good control | no data | good control | good control | good control | good control | bad control | bad control | bad control | bad control
| parameter steam | pH | Conductivity | Silica | [38 empty] | 132 | 0 | 1 | 2 | 1 | 2 | 3 | 4 | 5 | 6 | 7
| CONDENSATE TURBIN #3 | 100% | 100% | 100% | [38 empty] | 133 | parameter CT boiler house | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | chloride | turbidity
| parameter steam | pH | Conductivity | [39 empty] | 134 | COOLING TOWER BOILER HOUSE | no data | no data | no data | no data | no data | no data | no data | no data | no data
| CONDENSATE MPS PP | 100% | 100% | [39 empty] | 132: 135
| parameter steam | pH | Conductivity | [39 empty] | 132: 136
| CONDENSATE LPS PP | 100% | 100% | [39 empty] | 137 | POTENTIAL PROBLEM | 1 | 2 | 3 | 4 | 5
| parameter steam | pH | Conductivity | [39 empty] | 138 | parameter RO | pH | Conductivity | Total Hardness | Silica | Iron
| CONDENSATE MPS BH | stop | stop | [39 empty] | 132: 139; 0: RO TANK
| parameter steam | pH | Conductivity | [39 empty] | 140 | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| CONDENSATE HPS BH | stop | stop | [39 empty] | 141 | parameter xi'an | inlet FRC | pH Feed a | Conduct feed a | FRC feed a | Turbidity feed a | pH Feed b | Conduct feed b | FRC feed b | turbidity feed b | pH permeate a | conduct permeate a | silica permeate a | pH permeate b | conduct permeate b | silica permeate b | pH mix a | conduct mix a | hard mix a | silica mix a | iron mix a | pH mix b | conduct mix b | hard mix b | silica mix b | iron mix b
| parameter steam | pH | Conductivity | [39 empty] | 139 140: 142; RO TANK 0: RO XI'AN; RO TANK 3: no data; RO TANK 1: Corrosion in water line; RO TANK 2: scale potential in boiler, steam carryover potential; RO TANK 3: hardness scale potential in boiler; RO TANK 4: silica over limit in boiler, decrease boiler cycle of concentration; RO TANK 5: iron deposit potential in boiler; RO TANK 6: Corrosion in water line; RO TANK 7: scale potential in boiler, steam carryover potential; RO TANK 8: hardness scale potential in boiler; RO TANK 9: silica over limit in boiler, decrease boiler cycle of concentration; RO TANK 10: iron deposit potential in boiler
| CONDENSATE MPS GT | stop | stop | [39 empty] | 143 | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | [31 empty] | 144 | parameter yahua | inlet FRC | pH Feed | Conduct feed | FRC feed | Turbidity feed | pH permeate | conduct permeate | silica permeate | pH mix a | conduct mix a | hard mix a | silica mix a | iron mix a | pH mix b | conduct mix b | hard mix b | silica mix b | iron mix b
| parameter MIXBED #1 | pH mix a | conduct mix a | hard mix a | silica mix a | iron mix a | pH mix b | conduct mix b | hard mix b | silica mix b | iron mix b | [31 empty] | 145 | RO YAHUA | [7 empty] | no data | Corrosion in water line | scale potential in boiler, steam carryover potential | hardness scale potential in boiler | silica over limit in boiler, decrease boiler cycle of concentration | iron deposit potential in boiler | Corrosion in water line | scale potential in boiler, steam carryover potential | hardness scale potential in boiler | silica over limit in boiler, decrease boiler cycle of concentration | iron deposit potential in boiler
| MIXBED #1 | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | [31 empty] | 146 | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| parameter MIXBED #2 | pH mix a | conduct mix a | hard mix a | silica mix a | iron mix a | pH mix b | conduct mix b | hard mix b | silica mix b | iron mix b | [31 empty] | 147 | parameter jiangshu | inlet FRC | pH Feed a | Conduct feed a | FRC feed a | Turbidity feed a | pH Feed b | Conduct feed b | FRC feed b | turbidity feed b | pH permeate a | conduct permeate a | silica permeate a | pH permeate b | conduct permeate b | silica permeate b | pH mix a | conduct mix a | hard mix a | silica mix a | iron mix a | pH mix b | conduct mix b | hard mix b | silica mix b | iron mix b
| MIXBED #2 | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | [31 empty] | 148 | RO JIANGSHU | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | Corrosion in water line | scale potential in boiler, steam carryover potential | hardness scale potential in boiler | silica over limit in boiler, decrease boiler cycle of concentration | iron deposit potential in boiler | Corrosion in water line | scale potential in boiler, steam carryover potential | hardness scale potential in boiler | silica over limit in boiler, decrease boiler cycle of concentration | iron deposit potential in boiler
| parameter MIXBED #3 | pH mix a | conduct mix a | hard mix a | silica mix a | iron mix a | pH mix b | conduct mix b | hard mix b | silica mix b | iron mix b | [31 empty] | 0: BUFFER DEMIN; 1: 1; 1: 2; 2: 3; 3: 4
| MIXBED #3 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | [31 empty] | 0: Parameter Demin Tank; 1: pH; 1: Conductivity; 2: Silica; 3: Iron
| parameter MIXBED #4 | pH mix a | conduct mix a | hard mix a | silica mix a | iron mix a | [36 empty] | 0: DEMIN TANK; 3: corrosion in cooling tower
| MIXBED #4 | stop | stop | stop | stop | stop | [37 empty] | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3
[44 empty] | parameter dyn 1 | inlet FRC | pH Feed | Conduct feed | FRC feed | turbidity feed | pH permeate | conduct permeate | silica permeate
RO DYNALON 1
[44 empty] | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3
[44 empty] | parameter dyn 2 | inlet FRC | pH Feed | Conduct feed | FRC feed | turbidity feed | pH permeate | conduct permeate | silica permeate
[44 empty] | RO DYNALON 2 | [5 empty] | #NAME? | #NAME? | #NAME?
[44 empty] | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 1 | 2 | 3 | 4 | 5
[44 empty] | parameter dyn 4 | inlet FRC | pH Feed | Conduct feed | FRC feed | turbidity feed | pH permeate | conduct permeate | silica permeate | pH mix | conduct mix | hard mix | silica mix | iron mix
[44 empty] | RO DYNALON #4 | [5 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
[44 empty] | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3
[44 empty] | parameter new ro | inlet FRC | pH Feed | Conduct feed | FRC feed | turbidity feed | pH permeate | conduct permeate | silica permeate
[44 empty] | NEW RO | stop | stop | stop | stop | stop | #NAME? | #NAME? | #NAME?
[44 empty] | 0 | 1 | 2 | 3
|  | 1 | 2 | 4 | 5 | 3 | 6 | 1 | 2 | 3 | 4 | [32 empty] | 0: parameter domestic; 1: pH; 1: Conduct; 2: T.Hardness
| parameter boiler high pressure | pH FW | Conduct FW | Hardness FW | Turbidity FW | Iron FW | Surgard FW | pH Boiler | Conduct Boiler | Silica Boiler | PO4 Boiler | [32 empty] | 0: DOMESTIC TANK
| BOILER PP#1 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | [32 empty] | 0: parameter mixing; 1: pH; 1: Conduct; 2: T.Hardness
| parameter boiler high pressure | pH FW | Conduct FW | Hardness FW | Turbidity FW | Iron FW | Surgard FW | pH Boiler | Conduct Boiler | Silica Boiler | PO4 Boiler | [32 empty] | 0: MIXING TANK
| BOILER PP#2 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | [32 empty] | 0: parameter raw water; 1: pH; 1: Conduct; 2: T.Hardness
| parameter boiler high pressure | pH FW | Conduct FW | Hardness FW | Turbidity FW | Iron FW | Surgard FW | pH Boiler | Conduct Boiler | Silica Boiler | PO4 Boiler | [32 empty] | 0: RAW WATER TANK
| BOILER PP#3 | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | [32 empty] | 0: parameter raw water; 1: pH; 1: Conduct; 2: T.Hardness
| parameter boiler high pressure | pH FW | Conduct FW | Hardness FW | Turbidity FW | Iron FW | Surgard FW | pH Boiler | Conduct Boiler | Silica Boiler | PO4 Boiler | [32 empty] | 0: PDAM
| BOILER PP#4 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | [32 empty] | 0 | 1 | 1 | 1 | 1 | 2
| parameter boiler high pressure | pH FW | Conduct FW | Hardness FW | Turbidity FW | Iron FW | Surgard FW | pH Boiler | Conduct Boiler | Silica Boiler | PO4 Boiler | [32 empty] | parameter dyn 3 | FRC after biocide | FRC after 7408 | pH Feed | pH permeate | conduct permeate
| BOILER HP COAL | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | [32 empty] | DYNALON #3 | no data | no data | no data | no data | no data
| parameter boiler high pressure | pH FW | Conduct FW | Hardness FW | Turbidity FW | Iron FW | Surgard FW | pH Boiler | Conduct Boiler | Silica Boiler | PO4 Boiler | [32 empty] | parameteer brine 1 | FRC after biocide | FRC after 7408 | pH Feed | pH permeate | conduct permeate
| BOILER HP GAS | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | [32 empty] | RO BRINE #1 | no data | no data | no data | no data | no data
|  | 1 | 2 | 3 | 4 | 5 | 1 | 2 | 3 | 4 | 7 | 8 | [31 empty] | parameter brine 2 | FRC after biocide | FRC after 7408 | pH Feed | pH permeate | conduct permeate
| parameter low pressure | pH FW | Conduct FW | Hardness FW | Silica FW | Iron FW | pH Boiler | Conduct Boiler | O - Alkalinity | Silica Boiler | PO4 Boiler | Sulphite | [31 empty] | RO BRINE #2 | no data | no data | no data | no data | no data
| BOILER MP | stop | stop | no data | stop | stop | stop | stop | stop | stop | stop | stop | [31 empty] | parameter brine 3 | FRC after biocide | FRC after 7408 | pH Feed | pH permeate | conduct permeate
| parameter low pressure | pH FW | Conduct FW | Hardness FW | Silica FW | Iron FW | pH Boiler | Conduct Boiler | O - Alkalinity | Silica Boiler | PO4 Boiler | Sulphite | [31 empty] | RO Brine #3 | no data | no data | no data | no data | no data
| BOILER TOH #3 | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | [31 empty] | 0 | 1 | 2 | 3 | 4 | 5
| parameter low pressure | pH FW | Conduct FW | Hardness FW | Silica FW | Iron FW | pH Boiler | Conduct Boiler | O - Alkalinity | Silica Boiler | PO4 Boiler | Sulphite | [31 empty] | parameter demin tank | pH | Conductivity | Total Hardness | Silica | Iron
| BOILER TOH #4 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | [31 empty] | DEMIN TANK | no data | no data | no data | no data | no data
| parameter low pressure | pH FW | Conduct FW | Hardness FW | Silica FW | Iron FW | pH Boiler | Conduct Boiler | O - Alkalinity | Silica Boiler | PO4 Boiler | Sulphite | [31 empty] | parameter condensate | pH | Conductivity | Total Hardness | Silica | Iron
| BOILER HRSG #1 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | [31 empty] | 0: CONDENSATE TANK 200; 1: Corrosion in feed water line; 5: #REF!
| parameter low pressure | pH FW | Conduct FW | Hardness FW | Silica FW | Iron FW | pH Boiler | Conduct Boiler | O - Alkalinity | Silica Boiler | PO4 Boiler | Sulphite | [31 empty] | 0 | 1 | 2 | 3
| BOILER HRSG #2 | stop | stop | stop | stop | no data | stop | stop | stop | stop | stop | stop | [31 empty] | parameter steam | pH | Conductivity | Silica
| parameter low pressure | pH FW | Conduct FW | Hardness FW | Silica FW | Iron FW | pH Boiler | Conduct Boiler | O - Alkalinity | Silica Boiler | PO4 Boiler | Sulphite | [31 empty] | 0: CONDENSATE TURBIN #3
| BOILER OMNICAL | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | [31 empty] | 0: parameter steam; 1: pH; 2: Conductivity
|  | 1 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 2 | 3 | 1 | 2 | 1 | 2 | [28 empty] | 0: CONDENSATE MPS PP
| parameter sea water 1 | FRC In DAF | turbidity | turbidity | turbid in mmf | iron out mmf | turbidity out mmf | pH feed | iron | FRC | turbidity | pH Perm a | Cond Perm a | pH Perm b | Cond Perm b | [28 empty] | 0: parameter steam; 1: pH; 2: Conductivity
| SWRO 1 | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | [28 empty] | 0: CONDENSATE LPS PP
|  | 1 | 1 | 2 | 3 | 1 | 1 | 2 | 1 | 1 | 2 | 3 | 1 | 2 | 1 | 2 | [27 empty] | 0: parameter steam; 1: pH; 2: Conductivity
| parameter swro 2 | FRC In DAF | turbidity | turbidity | turbidity | turbid in mmf | iron out mmf | turbidity out mmf | pH feed | iron | FRC | turbidity | pH Perm a | Cond Perm a | pH Perm b | Cond Perm b | [27 empty] | 0: CONDENSATE MPS BH; 1: stop; 2: stop
| SWRO 2 | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | [27 empty] | 0: parameter steam; 1: pH; 2: Conductivity
| parameter swro 3 | FRC In DAF | turbidity | turbidity | turbidity | turbid in mmf | iron out mmf | turbidity out mmf | pH feed | iron | FRC | turbidity | pH Perm a | Cond Perm a | pH Perm b | Cond Perm b | [27 empty] | 0: CONDENSATE HPS BH; 1: stop; 2: stop
| SWRO 3 | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | 100% | 0% | [27 empty] | 0: parameter steam; 1: pH; 2: Conductivity
|  | 1 | 1 | 2 | 3 | 1 | 2 | [36 empty] | 0: CONDENSATE MPS GT; 1: stop; 2: stop
| parameter swro 4 | pH feed | iron | FRC | turbidity | pH Perm a | Cond Perm a | [36 empty] | 0: 0
| SWRO 4 | stop | stop | stop | stop | stop | stop | [36 empty] | 0: parameter MIXBED #1
|  | 1 | 2 | 1 | 2 | [38 empty] | 0: MIXBED #1 | [20 empty] | 1
| parameter product swro | pH pro 1 | Cond pro 1 | pH pro 5 | Cond pro 5 | [38 empty] | 0: parameter MIXBED #2
| PRODUCT SWRO | 100% | 0% | 100% | 0% | [38 empty] | 0: MIXBED #2
|  | 1 | 2 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | [31 empty] | parameter MIXBED #3
| parameter cooling tower | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | Orthophosphate (filter) | Free Chlorine | Chloride | Turbidity | [31 empty] | MIXBED #3
| COOLING TOWER GT 1 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | [31 empty] | parameter MIXBED #4
| parameter cooling tower | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | Orthophosphate (filter) | Free Chlorine | Chloride | Turbidity | [31 empty] | MIXBED #4
| COOLING TOWER GT 2 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | [31 empty] | 0 | [25 empty] | #REF!
| parameter cooling tower | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | Orthophosphate (filter) | Free Chlorine | Chloride | Turbidity | [31 empty] | 0
| COOLING TOWER PP | 100% | 100% | 100% | 100% | no data | 100% | no data | 100% | 100% | 100% | 100% | [31 empty] | 0
| parameter cooling tower | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | Orthophosphate (filter) | Free Chlorine | Chloride | Turbidity | [31 empty] | 0
| COOLING TOWER COMPRESSOR | 100% | 100% | 100% | 100% | no data | 100% | no data | 100% | 100% | 100% | 100% | [31 empty] | 0
|  | 1 | 2 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | [27 empty] | 0
| parameter CT boiler house | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | chloride | turbidity | [33 empty] | 0
| COOLING TOWER BOILER HOUSE | no data | no data | no data | no data | no data | no data | no data | no data | no data | [33 empty] | 0
0
0
0
0
[44 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | [17 empty] | parameter boiler high pressure | pH | Conductivity | T.hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate
|  | 1: 1; 2: 2; 3: 3; 4: 4; 5: 5 | [17 empty] | BOILER PP#1
|  | 1: pH; 2: Conductivity; 3: Total Hardness; 4: Silica; 5: Iron; 6: Chloride | [17 empty] | parameter boiler high pressure | pH | Conductivity | T.hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate
| RO TANK | [42 empty] | BOILER PP#2 | bar: 1 to 6
|  | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 5 | 6 | [10 empty] | 1 | [16 empty] | parameter boiler high pressure | pH | Conductivity | T.hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate
|  | inlet FRC | pH Feed a | Conduct feed a | FRC feed a | Turbidity feed a | pH Feed b | Conduct feed b | FRC feed b | turbidity feed b | pH permeate a | conduct permeate a | silica permeate a | pH permeate b | conduct permeate b | silica permeate b | [27 empty] | BOILER PP#3 | [6 empty] | stop | stop | stop | stop
| RO XI'AN | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | no data | 1 | 1 | 1 | [27 empty] | parameter boiler high pressure | pH | Conductivity | T.hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate
|  | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | [10 empty] | 1 | [16 empty] | BOILER PP#4
|  | 1: inlet FRC; 1: pH Feed; 2: Conduct feed; 3: FRC feed; 4: Turbidity feed; 1: pH permeate; 2: conduct permeate; 3: silica permeate | [27 empty] | parameter boiler high pressure | pH | Conductivity | T.hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate
| RO YAHUA | 1: 1; 1: 1; 2: 1; 3: 1; 4: 1; 1: 1; 2: 1; 3: no data | [27 empty] | BOILER HP COAL | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
|  | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 5 | 6 | [10 empty] | 1 | [16 empty] | parameter boiler high pressure | pH | Conductivity | T.hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate
|  | inlet FRC | pH Feed a | Conduct feed a | FRC feed a | Turbidity feed a | pH Feed b | Conduct feed b | FRC feed b | turbidity feed b | pH permeate a | conduct permeate a | silica permeate a | pH permeate b | conduct permeate b | silica permeate b | [27 empty] | BOILER HP GAS | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
| RO JIANGSHU | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | [27 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 1 | 2 | 3 | 4 | 5 | 6
|  | 1 | 2 | 3 | 4 | [21 empty] | stop | [16 empty] | parameter low pressure | pH | Conductivity | T.hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite
|  | pH | Conductivity | Total Hardness | Silica | iron | [37 empty] | BOILER MP | stop | stop | no data | stop | stop | stop | stop | stop | stop | stop | stop
| BUFFER DEMIN | 1 | 1 | no data | 1 | no data | [37 empty] | parameter low pressure | pH | Conductivity | T.hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite
|  | pH | Conductivity | Total Hardness | Silica | iron | [37 empty] | 0: BOILER TOH #3; 1: stop; 2: stop; 3: stop; 4: stop; 5: stop; 6: stop
| DEMIN TANK | 1 | 1 | 1 | 0 | 1 | [37 empty] | parameter low pressure | pH | Conductivity | T.hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite
|  | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | [17 empty] | 0.75 | [16 empty] | BOILER TOH #4
|  | inlet FRC | pH Feed | Conduct feed | FRC feed | turbidity feed | pH permeate | conduct permeate | silica permeate | [34 empty] | parameter low pressure | pH | Conductivity | T.hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite
| RO DYNALON 1 | [42 empty] | BOILER HRSG #1 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | bar: 1 to 3
|  | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | [17 empty] | 1 | [16 empty] | parameter low pressure | pH | Conductivity | T.hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite
|  | inlet FRC | pH Feed | Conduct feed | FRC feed | turbidity feed | pH permeate | conduct permeate | silica permeate | [34 empty] | BOILER HRSG #2 | stop | stop | stop | stop | no data | stop | stop | stop | stop | stop | stop
| RO DYNALON 2 | 1 | 1 | 1 | 1 | 1 | #NAME? | #NAME? | #NAME? | [34 empty] | parameter low pressure | pH | Conductivity | T.hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite
|  | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | [34 empty] | BOILER OMNICAL |  |  |  |  | no data
|  | inlet FRC | pH Feed | Conduct feed | FRC feed | turbidity feed | pH permeate | conduct permeate | silica permeate | [34 empty] | 0 | 1 | 1 | 2 | 3 | 1 | 1 | 2 | 1 | 1 | 2 | 3 | 1 | 2 | 1 | 2
| RO DYNALON #4 | 1 | 1 | 1 | 1 | 1 | #NAME? | #NAME? | #NAME? | [34 empty] | parameter sea water 1 | FRC | FRC | turbidity | turbidity | turbidity inlet mmf | iron outlet mmf | turbidity outlet mmf | pH feed | iron | FRC | turbidity | pH permeate a | Cond permeate a | pH permeate b | Cond permeate b
|  | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | [34 empty] | SWRO 1 | stop | [11 empty] | stop | stop | wtp membrane is not optimal
|  | inlet FRC | pH Feed | Conduct feed | FRC feed | turbidity feed | pH permeate | conduct permeate | silica permeate | [34 empty] | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 1 | 2 | 1 | 1 | 2 | 3 | 1 | 2 | 1 | 2
| NEW RO | stop | stop | stop | stop | stop | #NAME? | #NAME? | #NAME? | [34 empty] | parameter swro 2 | FRC | FRC | turbidity | turbidity | turbidity | turbidity inlet mmf | iron outlet mmf | turbidity outlet mmf | pH feed | iron | FRC | turbidity | pH permeate a | Cond permeate a | pH permeate b | Cond permeate b
|  | 1 | 2 | 3 | 4 | 5 | 1 | 2 | 3 | 4 | 5 | [15 empty] | stop | [16 empty] | SWRO 2 |  | bacterial growth increases (under limit), wasteful of chemicals (over limit) | carryover to the next process | carryover to the next process | carryover to the next process | [10 empty] | wtp membrane is not optimal
| MIXBED #1 | pH mix a | conduct mix a | hard mix a | silica mix a | iron mix a | pH mix b | conduct mix b | hard mix b | silica mix b | iron mix b | [32 empty] | parameter swro 3 | FRC | FRC | turbidity | turbidity | turbidity | turbidity inlet mmf | iron outlet mmf | turbidity outlet mmf | pH feed | iron | FRC | turbidity | pH permeate a | Cond permeate a | pH permeate b | Cond permeate b
|  | 1 | 1 | 1 | 1 | 1 | 1 | stop | stop | stop | stop | [15 empty] | 1 | [16 empty] | SWRO 3 |  | #REF! |  |  |  | The effect is wasteful of water for frequent backwashing, can interfere with operational running | [6 empty] | stop | stop |  | wtp membrane is not optimal
| MIXBED #2 | pH mix a | conduct mix a | hard mix a | silica mix a | iron mix a | pH mix b | conduct mix b | hard mix b | silica mix b | iron mix b | [32 empty] | 0 | 1 | 1 | 2 | 3 | 1 | 2
|  | stop | stop | stop | stop | stop | stop | 1 | 1 | 1 | 1 | [15 empty] | stop | [16 empty] | parameter swro 4 | pH feed | iron | FRC | turbidity | pH permeate a | Cond permeate a
| MIXBED #3 | pH mix a | conduct mix a | hard mix a | silica mix a | iron mix a | pH mix b | conduct mix b | hard mix b | silica mix b | iron mix b | [32 empty] | SWRO 4 | stop | stop | stop | stop | stop | stop
|  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | [32 empty] | 0 | 1 | 2 | 1 | 2
| MIXBED #4 | 1: pH mix a; 2: conduct mix a; 3: hard mix a; 4: silica mix a; 5: iron mix a | [32 empty] | parameter product swro | pH pro 1 | Cond pro 1 | pH pro 234 | Cond pro 234
|  | 1: stop; 2: stop; 3: stop; 4: stop; 5: stop | [15 empty] | stop | [16 empty] | PRODUCT SWRO |  | wtp membrane is not optimal |  | wtp membrane is not optimal
|  | pH | Conduct | T.Hardness | [39 empty] | 0 | 1 | 2 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
| DOMESTIC TANK | 1 | 1 | 1 | [39 empty] | parameter cooling tower | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | Zinc | Orthophosphate (filter) | Free Chlorine | Active Polymer | Aluminium | Chloride | Turbidity | TAB
|  | pH | Conduct | T.Hardness | [39 empty] | COOLING TOWER GT 1 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | fouling in HE | corrosion in line water | fouling in system cooling tower | inhibits heat transfer
| MIXING TANK | 1 | 1 | 1 | [39 empty] | parameter cooling tower | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | Zinc | Orthophosphate (filter) | Free Chlorine | Active Polymer | Aluminium | Chloride | Turbidity | TAB
|  | pH | Conduct | T.Hardness | [22 empty] | 1 | [16 empty] | COOLING TOWER GT 2 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | fouling in HE | corrosion in line water | fouling in system cooling tower | inhibits heat transfer
| RAW WATER TANK | 1 | 1 | 1 | [39 empty] | parameter cooling tower | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | Zinc | Orthophosphate (filter) | Free Chlorine | Active Polymer | Aluminium | Chloride | Turbidity | TAB
|  | pH | Conduct | T.Hardness | [22 empty] | 1 | [16 empty] | PRODUCT SWRO 0: COOLING TOWER PP; wtp membrane is not optimal 3: no data; wtp membrane is not optimal 5: no data; wtp membrane is not optimal 10: fouling in HE; wtp membrane is not optimal 11: corrosion in line water; wtp membrane is not optimal 12: fouling in system cooling tower; wtp membrane is not optimal 13: inhibits heat transfer
| PDAM | 1 | 1 | 1 | [39 empty] | parameter cooling tower | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | Zinc | Orthophosphate (filter) | Free Chlorine | Active Polymer | Aluminium | Chloride | Turbidity | TAB
|  | 1 | 1 | 1 | 1 | 2 | [20 empty] | 1 | [16 empty] | PRODUCT SWRO 0: COOLING TOWER COMPRESSOR; wtp membrane is not optimal 3: no data; wtp membrane is not optimal 5: no data; wtp membrane is not optimal 10: fouling in HE; wtp membrane is not optimal 11: corrosion in line water; wtp membrane is not optimal 12: fouling in system cooling tower; wtp membrane is not optimal 13: inhibits heat transfer
|  | FRC after biocide | FRC after 7408 | pH Feed | pH permeate | conduct permeate | [37 empty] | 0 | 1 | 2 | 1 | 2 | 3 | 4 | 5 | 6 | 7
| DYNALON #3 | no data | no data | no data | no data | no data | [37 empty] | parameter CT boiler house | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | chloride | turbidity
|  | FRC after biocide | FRC after 7408 | pH Feed | pH permeate | conduct permeate | [37 empty] | COOLING TOWER BOILER HOUSE | no data | no data | no data | no data | no data | no data | no data | no data | no data
| RO BRINE #1 | no data | no data | no data | no data | no data
|  | FRC after biocide | FRC after 7408 | pH Feed | pH permeate | conduct permeate | [37 empty] | ROOT CAUSE | 1 | 2 | 3 | 4 | 5
| RO BRINE #2 | no data | no data | no data | no data | no data | [37 empty] | parameter RO | pH | Conductivity | Total Hardness | Silica | Iron
|  | FRC after biocide | FRC after 7408 | pH Feed | pH permeate | conduct permeate | [37 empty] | COOLING TOWER COMPRESSOR 0: RO TANK
| RO Brine #3 | no data | no data | no data | no data | no data | [36 empty] | 1 | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
|  | 1 | 1 | 1 | 1 | [37 empty] | 2 | parameter xi'an | inlet FRC | pH Feed a | Conduct feed a | FRC feed a | Turbidity feed a | pH Feed b | Conduct feed b | FRC feed b | turbidity feed b | pH permeate a | conduct permeate a | silica permeate a | pH permeate b | conduct permeate b | silica permeate b | pH mix a | conduct mix a | hard mix a | silica mix a | iron mix a | pH mix b | conduct mix b | hard mix b | silica mix b | iron mix b
|  | Temp.PP#1 | Temp.PP#2 | Temp.PP#3 | Temp.PP#4 | [37 empty] | 1: 3; RO TANK 0: RO XI'AN; RO TANK 3: no data; RO TANK 1: pH quality permeate; RO TANK 2: quality conductivity permeate RO is bad, not optimal regeneration mixbed; RO TANK 3: not optimal regeneration mixbed; RO TANK 4: not optimal regeneration mixbed; RO TANK 5: not optimal regeneration mixbed, saturation of resin; RO TANK 6: pH quality permeate; RO TANK 7: quality conductivity permeate RO is bad, not optimal regeneration mixbed; RO TANK 8: not optimal regeneration mixbed; RO TANK 9: not optimal regeneration mixbed; RO TANK 10: not optimal regeneration mixbed, saturation of resin
| #REF! | #REF! | #REF! | #REF! | #REF! | [37 empty] | 4 | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
|  | 1 | 2 | [39 empty] | 5 | parameter yahua | inlet FRC | pH Feed | Conduct feed | FRC feed | Turbidity feed | pH permeate | conduct permeate | silica permeate | pH mix a | conduct mix a | hard mix a | silica mix a | iron mix a | pH mix b | conduct mix b | hard mix b | silica mix b | iron mix b
|  | Temp | Temp | [39 empty] | 6 | RO YAHUA | [7 empty] | no data | pH quality permeate | quality conductivity permeate RO is bad, not optimal regeneration mixbed | not optimal regeneration mixbed | not optimal regeneration mixbed | not optimal regeneration mixbed, saturation of resin | pH quality permeate | quality conductivity permeate RO is bad, not optimal regeneration mixbed | not optimal regeneration mixbed | not optimal regeneration mixbed | not optimal regeneration mixbed, saturation of resin
| #REF! | #REF! | [40 empty] | 7 | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
[27 empty] | #REF! | [15 empty] | 8 | parameter jiangshu | inlet FRC | pH Feed a | Conduct feed a | FRC feed a | Turbidity feed a | pH Feed b | Conduct feed b | FRC feed b | turbidity feed b | pH permeate a | conduct permeate a | silica permeate a | pH permeate b | conduct permeate b | silica permeate b | pH mix a | conduct mix a | hard mix a | silica mix a | iron mix a | pH mix b | conduct mix b | hard mix b | silica mix b | iron mix b
|  | Temp | [40 empty] | 9 | RO JIANGSHU | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | pH quality permeate | quality conductivity permeate RO is bad, not optimal regeneration mixbed | not optimal regeneration mixbed | not optimal regeneration mixbed | not optimal regeneration mixbed, saturation of resin | pH quality permeate | quality conductivity permeate RO is bad, not optimal regeneration mixbed | not optimal regeneration mixbed | not optimal regeneration mixbed | not optimal regeneration mixbed, saturation of resin
| #REF! | #REF! | [40 empty] | 7: 10; 0: BUFFER DEMIN; 1: 1; 1: 2; 2: 3; 3: 4
|  | Temp | [24 empty] | #REF! | [15 empty] | 7: 11; 0: Parameter Demin Tank; 1: pH; 1: Conductivity; 2: Silica; 3: Iron
| #REF! | #REF! | [40 empty] | 7: 12; 0: DEMIN TANK; 3: quality permeate RO is bad
|  | Temp | [24 empty] | #REF! | [15 empty] | 7: 13; 0: 0; 1: 1; 1: 1; 2: 2; 3: 3; 4: 4; 1: 1; 2: 2; 3: 3
| #REF! | #REF! | [40 empty] | 7: 14; 0: parameter dyn 1; 1: inlet FRC; 1: pH Feed; 2: Conduct feed; 3: FRC feed; 4: turbidity feed; 1: pH permeate; 2: conduct permeate; 3: silica permeate
|  | 1 | 1 | [23 empty] | #REF! | [15 empty] | 7: 15; 0: RO DYNALON 1
|  | Temp.HRSG#1 | Temp.HRSG#2 | [39 empty] | 7: 16; 0: 0; 1: 1; 1: 1; 2: 2; 3: 3; 4: 4; 1: 1; 2: 2; 3: 3
| #REF! | #REF! | #REF! | [23 empty] | #REF! | [15 empty] | 7: 17; 0: parameter dyn 2; 1: inlet FRC; 1: pH Feed; 2: Conduct feed; 3: FRC feed; 4: turbidity feed; 1: pH permeate; 2: conduct permeate; 3: silica permeate
|  | 1 | 2 | 3 | 4 | 5 | [36 empty] | 7: 18; 0: RO DYNALON 2; 1: #NAME?; 2: #NAME?; 3: #NAME?
|  | pH | Conductivity | Total Hardness | Silica | Iron | [36 empty] | 19 | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 1 | 2 | 3 | 4 | 5
| DEMIN TANK | no data | no data | no data | no data | no data | [20 empty] | #REF! | [15 empty] | 20 | parameter dyn 4 | inlet FRC | pH Feed | Conduct feed | FRC feed | turbidity feed | pH permeate | conduct permeate | silica permeate | pH mix | conduct mix | hard mix | silica mix | iron mix
|  | pH | Conductivity | Total Hardness | Silica | Iron | [36 empty] | 21 | RO DYNALON #4 | [5 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
| CONDENSATE TANK 200 | 0 | 1 | 1 | 1 | #REF! | [36 empty] | 22 | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3
|  | 1 | 2 | 3 | [38 empty] | 23 | parameter new ro | inlet FRC | pH Feed | Conduct feed | FRC feed | turbidity feed | pH permeate | conduct permeate | silica permeate
|  | pH | Conductivity | Silica | [38 empty] | 24 | NEW RO | stop | stop | stop | stop | stop | #NAME? | #NAME? | #NAME?
| CONDENSATE TURBIN #3 | 1 | 1 | 1 | [38 empty] | 18 19: 25; RO DYNALON 2 0: 0; RO DYNALON 2 1: 1; RO DYNALON 2 1: 2; RO DYNALON 2 2: 3
|  | pH | Conductivity | [39 empty] | 18 19: 26; RO DYNALON 2 0: parameter domestic; RO DYNALON 2 1: pH; RO DYNALON 2 1: Conduct; RO DYNALON 2 2: T.Hardness
| CONDENSATE MPS PP | 1 | 1 | [39 empty] | 18 19: 27; RO DYNALON 2 0: DOMESTIC TANK
|  | pH | Conductivity | [23 empty] | 1 | [15 empty] | 18 19: 28; RO DYNALON 2 0: parameter mixing; RO DYNALON 2 1: pH; RO DYNALON 2 1: Conduct; RO DYNALON 2 2: T.Hardness
| CONDENSATE LPS PP | 1 | 1 | [39 empty] | 18 19: 29; RO DYNALON 2 0: MIXING TANK
|  | pH | Conductivity | [23 empty] | 1 | [15 empty] | 18 19: 30; RO DYNALON 2 0: parameter raw water; RO DYNALON 2 1: pH; RO DYNALON 2 1: Conduct; RO DYNALON 2 2: T.Hardness
| CONDENSATE MPS BH | stop | stop | [39 empty] | 18 19: 31; RO DYNALON 2 0: RAW WATER TANK
|  | pH | Conductivity | [23 empty] | 1 | [15 empty] | 18 19: 32; RO DYNALON 2 0: parameter raw water; RO DYNALON 2 1: pH; RO DYNALON 2 1: Conduct; RO DYNALON 2 2: T.Hardness
| CONDENSATE HPS BH | stop | stop | [39 empty] | 18 19: 33; RO DYNALON 2 0: PDAM
|  | pH | Conductivity | [23 empty] | stop | [15 empty] | 18 19: 34; RO DYNALON 2 0: 0; RO DYNALON 2 1: 1; RO DYNALON 2 1: 1; RO DYNALON 2 2: 1; RO DYNALON 2 3: 1; RO DYNALON 2 4: 2
| CONDENSATE MPS GT | stop | stop | [39 empty] | 18 19: 35; RO DYNALON 2 0: parameter dyn 3; RO DYNALON 2 1: FRC after biocide; RO DYNALON 2 1: FRC after 7408; RO DYNALON 2 2: pH Feed; RO DYNALON 2 3: pH permeate; RO DYNALON 2 4: conduct permeate
[27 empty] | stop | [15 empty] | 18 19: 36; RO DYNALON 2 0: DYNALON #3; RO DYNALON 2 1: no data; RO DYNALON 2 1: no data; RO DYNALON 2 2: no data; RO DYNALON 2 3: no data; RO DYNALON 2 4: no data
[43 empty] | 37 | parameteer brine 1 | FRC after biocide | FRC after 7408 | pH Feed | pH permeate | conduct permeate
| 0 | stop | stop | stop | stop | [37 empty] | 18 19: 38; RO DYNALON 2 0: RO BRINE #1; RO DYNALON 2 1: no data; RO DYNALON 2 1: no data; RO DYNALON 2 2: no data; RO DYNALON 2 3: no data; RO DYNALON 2 4: no data
|  |  |  | Silica | [38 empty] | 18 19: 39; RO DYNALON 2 0: parameter brine 2; RO DYNALON 2 1: FRC after biocide; RO DYNALON 2 1: FRC after 7408; RO DYNALON 2 2: pH Feed; RO DYNALON 2 3: pH permeate; RO DYNALON 2 4: conduct permeate
| 0 |  |  | stop | [38 empty] | 18 19: 40; RO DYNALON 2 0: RO BRINE #2; RO DYNALON 2 1: no data; RO DYNALON 2 1: no data; RO DYNALON 2 2: no data; RO DYNALON 2 3: no data; RO DYNALON 2 4: no data
|  | pH | Conductivity | Silica | [38 empty] | 18 19: 41; RO DYNALON 2 0: parameter brine 3; RO DYNALON 2 1: FRC after biocide; RO DYNALON 2 1: FRC after 7408; RO DYNALON 2 2: pH Feed; RO DYNALON 2 3: pH permeate; RO DYNALON 2 4: conduct permeate
| 0 | 1 | 1 | 1 | [38 empty] | 18 19: 42; RO DYNALON 2 0: RO Brine #3; RO DYNALON 2 1: no data; RO DYNALON 2 1: no data; RO DYNALON 2 2: no data; RO DYNALON 2 3: no data; RO DYNALON 2 4: no data
|  | pH | Conductivity | Silica | [22 empty] | stop | [15 empty] | 43 | 0 | 1 | 2 | 3 | 4 | 5
| 0 | stop | stop | stop | [38 empty] | 44 | parameter demin tank | pH | Conductivity | Total Hardness | Silica | Iron
|  | pH | Conductivity | Silica | [22 empty] | 1 | [15 empty] | 45 | DEMIN TANK | no data | no data | no data | no data | no data
| 0 | stop | stop | stop | [38 empty] | 46 | parameter condensate | pH | Conductivity | Total Hardness | Silica | Iron
|  | pH | Conductivity | Silica | [22 empty] | stop | [15 empty] | 43: 47; 0: CONDENSATE TANK 200; 1: inproper injection point, inproper dosage chemical, contamination; 5: #REF!
| 0 | 1 | 1 | 1 | [38 empty] | 48 | 0 | 1 | 2 | 3
|  | 1 | 2 | 4 | 5 | 3 | 6 | 1 | 2 | 3 | 4 | [15 empty] | stop | [15 empty] | 49 | parameter steam | pH | Conductivity | Silica
|  | pH | Conductivity | T. Hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate | [31 empty] | 43: 50; 0: CONDENSATE TURBIN #3
| BOILER PP#1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [15 empty] | 1 | [15 empty] | 43: 51; 0: parameter steam; 1: pH; 2: Conductivity
|  | pH | Conductivity | T. Hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate | [31 empty] | 43: 52; 0: CONDENSATE MPS PP
| BOILER PP#2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [31 empty] | 43: 53; 0: parameter steam; 1: pH; 2: Conductivity
|  | pH | Conductivity | T. Hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate | [15 empty] | 1 | [15 empty] | 43: 54; 0: CONDENSATE LPS PP
| BOILER PP#3 | 1 | 1 | 1 | 1 | 1 | 1 | stop | stop | stop | stop | [31 empty] | 43: 55; 0: parameter steam; 1: pH; 2: Conductivity
|  | pH | Conductivity | T. Hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate | [15 empty] | 1 | [15 empty] | 43: 56; 0: CONDENSATE MPS BH; 1: stop; 2: stop
| BOILER PP#4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [31 empty] | 43: 57; 0: parameter steam; 1: pH; 2: Conductivity
|  | pH | Conductivity | T. Hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate | [15 empty] | 1 | [15 empty] | 43: 58; 0: CONDENSATE HPS BH; 1: stop; 2: stop
| BOILER HP COAL | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | [31 empty] | 43: 59; 0: parameter steam; 1: pH; 2: Conductivity
|  | pH | Conductivity | T. Hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate | [15 empty] | 1 | [15 empty] | 43: 60; 0: CONDENSATE MPS GT; 1: stop; 2: stop
| BOILER HP GAS | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | [31 empty] | 43: 61; 0: parameter MIXBED #1
|  | 1 | 2 | 3 | 4 | 5 | 1 | 2 | 3 | 4 | 5 | 6 | [14 empty] | stop | [15 empty] | 62 | MIXBED #1
|  | pH | Conductivity | T. Hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite | [30 empty] | 63 | parameter MIXBED #2
| BOILER MP | stop | stop | no data | stop | stop | stop | stop | stop | stop | stop | stop | [14 empty] | stop | [15 empty] | 64 | MIXBED #2
|  | pH | Conductivity | T. Hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite | [30 empty] | 65 | parameter MIXBED #3
| BOILER TOH #3 | 1 | 1 | 1 | 1 | 1 | stop | stop | stop | stop | stop | stop | [30 empty] | 66 | MIXBED #3
|  | pH | Conductivity | T. Hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite | [14 empty] | stop | [15 empty] | 67 | parameter MIXBED #4
| BOILER TOH #4 | [41 empty] | 68 | MIXBED #4 | bar: 1 to 6
|  | pH | Conductivity | T. Hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite | [14 empty] | 1 | [15 empty] | 69 | 0
| BOILER HRSG #1 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | [30 empty] | 70 | 0
|  | pH | Conductivity | T. Hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite | [14 empty] | 1 | [15 empty] | 71 | 0
| BOILER HRSG #2 | stop | stop | stop | stop | no data | stop | stop | stop | stop | stop | stop | [30 empty] | 72 | 0
|  | pH | Conductivity | T. Hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite | [14 empty] | stop | [15 empty] | 73 | 0
| BOILER OMNICAL | 1 | 1 | 1 | 1 | no data | 1 | 1 | 1 | 1 | 1 | 1 | [30 empty] | 74 | 0
|  | 1 | 1 | 2 | 3 | 1 | 1 | 2 | 1 | 1 | 2 | 3 | 1 | 2 | [12 empty] | stop | [15 empty] | 75 | 0
|  | FRC | FRC | turbidity | turbidity | turbidity inlet mmf | iron outlet mmf | turbidity outlet mmf | pH feed | iron | FRC | turbidity | pH | Cond | [28 empty] | 76 | 0
| SWRO 1 | stop | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | stop | [12 empty] | 1 | [15 empty] | 77 | 0
|  | 1 | 1 | 2 | 3 | 4 | 1 | 1 | 2 | 1 | 1 | 2 | 3 | 1 | 2 | 1 | 2 | [25 empty] | 78 | 0
|  | FRC | turbidity | turbidity | turbidity | turbidity inlet mmf | iron outlet mmf | turbidity outlet mmf | pH feed | iron | FRC | turbidity | pH Perm a | Cond Perm a | pH Perm b | Cond Perm b | [26 empty] | 79 | 0
| SWRO 2 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [10 empty] | stop | [15 empty] | 80 | 0
|  | FRC | turbidity | turbidity | turbidity | turbidity inlet mmf | iron outlet mmf | turbidity outlet mmf | pH feed | iron | FRC | turbidity | pH Perm a | Cond Perm a | pH Perm b | Cond Perm b | [26 empty] | 81 | 0
| SWRO 3 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | stop | stop | 1 | 0 | [26 empty] | 82 | parameter boiler high pressure | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4
|  | 1: 1; 2: 1; 3: 2; 4: 3; 5: 1; 1: 2 | [14 empty] | 0.733 | [15 empty] | 83 | BOILER PP#1 | pH | Conductivity | T. Hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate
|  | 1: pH feed; 2: iron; 3: FRC; 4: turbidity; 5: pH mix a; 1: Cond mix a | [30 empty] | 84 | parameter boiler high pressure
| SWRO 4 | 1: stop; 2: stop; 3: stop; 4: stop; 5: stop; 1: stop | [14 empty] | 0.846 | [15 empty] | 85 | BOILER PP#2 | pH | Conductivity | T. Hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate
|  | 1: 1; 2: 2; 3: 1; 4: 2 | [30 empty] | 86 | parameter boiler high pressure
|  | 1: pH pro 1; 2: Cond pro 1; 3: pH pro 5; 4: Cond pro 5 | [30 empty] | 87 | BOILER PP#3 | pH | Conductivity | T. Hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate
| PRODUCT SWRO | 1: 1; 2: 0; 3: 1; 4: 0 | [14 empty] | stop | [15 empty] | 88 | parameter boiler high pressure | [6 empty] | stop | stop | stop | stop
|  | 1 | 2 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | [30 empty] | 89 | BOILER PP#4 | pH | Conductivity | T. Hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate
|  | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | Orthophosphate (filter) | Free Chlorine | Chloride | Turbidity | [30 empty] | 90 | parameter boiler high pressure
| COOLING TOWER GT 1 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | [14 empty] | 0.5 | [15 empty] | 91 | BOILER HP COAL | pH | Conductivity | T. Hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate
|  | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | Orthophosphate (filter) | Free Chlorine | Chloride | Turbidity | [30 empty] | 92 | parameter boiler high pressure | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
| COOLING TOWER GT 2 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | [30 empty] | 93 | BOILER HP GAS | pH | Conductivity | T. Hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate
|  | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | Orthophosphate (filter) | Free Chlorine | Chloride | Turbidity | [14 empty] | stop | [15 empty] | 94 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
| COOLING TOWER PP | 1 | 1 | 1 | 1 | no data | 1 | no data | 1 | 1 | 1 | 1 | [30 empty] | 95 | parameter low pressure | 1 | 2 | 3 | 4 | 5 | 1 | 2 | 3 | 4 | 5 | 6
|  | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | Orthophosphate (filter) | Free Chlorine | Chloride | Turbidity | [14 empty] | stop | [15 empty] | 96 | BOILER MP | pH | Conductivity | T. Hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite
| COOLING TOWER COMPRESSOR | 1 | 1 | 1 | 1 | no data | 1 | no data | 1 | 1 | 1 | 1 | [30 empty] | 97 | parameter low pressure | stop | stop | no data | stop | stop | stop | stop | stop | stop | stop | stop
|  | 1 | 2 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | [16 empty] | 1 | [15 empty] | 98 | BOILER TOH #3 | pH | Conductivity | T. Hardness | Silica |  | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite
|  | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | chloride | turbidity | [32 empty] | 99 | parameter low pressure | [5 empty] | stop | stop | stop | stop | stop | stop
| COOLING TOWER BOILER HOUSE | no data | no data | no data | no data | no data | no data | no data | no data | no data | [16 empty] | 1 | [15 empty] | 100 | BOILER TOH #4 | pH | Conductivity | T. Hardness | Silica |  | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite
[43 empty] | 101 | parameter low pressure
[43 empty] | 102 | BOILER HRSG #1 | pH | Conductivity | T. Hardness | Silica |  | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite
|  | 1 | 2 | 4 | 5 | 3 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | [16 empty] | 103 | parameter low pressure | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
[43 empty] | 104 | BOILER HRSG #2 | pH | Conductivity | T. Hardness | Silica |  | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite
| RO TANK | [41 empty] | 105 | parameter low pressure | stop | stop | stop | stop | no data | stop | stop | stop | stop | stop | stop
| RO XI'AN | [41 empty] | 106 | BOILER OMNICAL | pH | Conductivity | T. Hardness | Silica |  | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite
| RO YAHUA | [41 empty] | 107 | 0 |  |  |  |  | no data
| RO JIANGSHU | [41 empty] | 108 | parameter sea water 1 | 1 | 1 | 2 | 3 | 1 | 1 | 2 | 1 | 1 | 2 | 3 | 1 | 2 | 1 | 2
| BUFFER DEMIN | [41 empty] | 109 | SWRO 1 | FRC | FRC | turbidity | turbidity | turbidity inlet mmf | iron outlet mmf | turbidity outlet mmf | pH feed | iron | FRC | turbidity | pH permeate a | Cond permeate a | pH permeate b | Cond permeate b
| DEMIN TANK | 5: Silica | [16 empty] | 110 | 0 | stop | [11 empty] | stop | stop | inproper quality conductivity feed RO, broken membrane RO, seal vessel leak out
| RO DYNALON 1 | [41 empty] | 111 | parameter swro 2 | 1 | 1 | 2 | 3 | 4 | 1 | 1 | 2 | 1 | 1 | 2 | 3 | 1 | 2 | 1 | 2
| RO DYNALON 2 | 6: #NAME?; 7: #NAME?; 8: #NAME? | [16 empty] | 112 | SWRO 2 | FRC | FRC | turbidity | turbidity | turbidity | turbidity inlet mmf | iron outlet mmf | turbidity outlet mmf | pH feed | iron | FRC | turbidity | pH permeate a | Cond permeate a | pH permeate b | Cond permeate b
| RO DYNALON #4 | 6: #NAME?; 7: #NAME?; 8: #NAME? | [16 empty] | 113 | parameter swro 3 |  | inproper injection point, inproper dosage, problem in injection line | turbidity from inlet DAF high,inproper dosage chemical | turbidity from inlet DAF high,inproper dosage chemical | turbidity from inlet DAF high,inproper dosage chemical | [10 empty] | inproper quality conductivity feed RO, broken membrane RO, seal vessel leak out
| NEW RO | 6: #NAME?; 7: #NAME?; 8: #NAME? | [16 empty] | 114 | SWRO 3 | FRC | FRC | turbidity | turbidity | turbidity | turbidity inlet mmf | iron outlet mmf | turbidity outlet mmf | pH feed | iron | FRC | turbidity | pH permeate a | Cond permeate a | pH permeate b | Cond permeate b
| MIXBED #1 | [41 empty] | 115 | 0 |  | #REF! |  |  |  | turbidity from outlet DAF high,inproper dosage chemical | [6 empty] | stop | stop |  | inproper quality conductivity feed RO, broken membrane RO, seal vessel leak out
| MIXBED #2 | [41 empty] | 116 | parameter swro 4 | 1 | 1 | 2 | 3 | 1 | 2
| MIXBED #3 | [41 empty] | 117 | SWRO 4 | pH feed | iron | FRC | turbidity | pH permeate a | Cond permeate a
| MIXBED #4 | [41 empty] | 118 | 0 | stop | stop | stop | stop | stop | stop
| DOMESTIC TANK | [41 empty] | 119 | parameter product swro | 1 | 2 | 1 | 2
| MIXING TANK | [41 empty] | 120 | PRODUCT SWRO | pH pro 1 | Cond pro 1 | pH pro 234 | Cond pro 234
| RAW WATER TANK | [41 empty] | 121 | 0 |  | inproper quality conductivity feed RO, broken membrane RO, seal vessel leak out |  | inproper quality conductivity feed RO, broken membrane RO, seal vessel leak out
| PDAM | [41 empty] | 122 | parameter cooling tower | 1 | 2 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
| DYNALON #3 | [41 empty] | 123 | COOLING TOWER GT 1 | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | Zinc | Orthophosphate (filter) | Free Chlorine | Active Polymer | Aluminium | Chloride | Turbidity | TAB
| RO BRINE #1 | [41 empty] | 124 | parameter cooling tower | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | inproper sampling point,inproper dosage chemical,aluminium content make up | inproper sampling point,chloride content make up high, less blowdown | inproper sampling point,contamination,less blowdown | inproper dosage chemical,contamination,less blowdown
| RO BRINE #2 | [41 empty] | 125 | COOLING TOWER GT 2 | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | Zinc | Orthophosphate (filter) | Free Chlorine | Active Polymer | Aluminium | Chloride | Turbidity | TAB
| RO Brine #3 | [41 empty] | 126 | parameter cooling tower | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | inproper sampling point,inproper dosage chemical,aluminium content make up | inproper sampling point,chloride content make up high, less blowdown | inproper sampling point,contamination,less blowdown | inproper dosage chemical,contamination,less blowdown
| #REF! | #REF! | [40 empty] | 127 | COOLING TOWER PP | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | Zinc | Orthophosphate (filter) | Free Chlorine | Active Polymer | Aluminium | Chloride | Turbidity | TAB
| #REF! | #REF! | [40 empty] | 128 | parameter cooling tower | inproper quality conductivity feed RO, broken membrane RO, seal vessel leak out 3: no data; inproper quality conductivity feed RO, broken membrane RO, seal vessel leak out 5: no data; inproper quality conductivity feed RO, broken membrane RO, seal vessel leak out 10: inproper sampling point,inproper dosage chemical,aluminium content make up; inproper quality conductivity feed RO, broken membrane RO, seal vessel leak out 11: inproper sampling point,chloride content make up high, less blowdown; inproper quality conductivity feed RO, broken membrane RO, seal vessel leak out 12: inproper sampling point,contamination,less blowdown; inproper quality conductivity feed RO, broken membrane RO, seal vessel leak out 13: inproper dosage chemical,contamination,less blowdown
| #REF! | #REF! | [40 empty] | 129 | COOLING TOWER COMPRESSOR | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | Zinc | Orthophosphate (filter) | Free Chlorine | Active Polymer | Aluminium | Chloride | Turbidity | TAB
| #REF! | #REF! | [40 empty] | 130 | 0 | inproper quality conductivity feed RO, broken membrane RO, seal vessel leak out 3: no data; inproper quality conductivity feed RO, broken membrane RO, seal vessel leak out 5: no data; inproper quality conductivity feed RO, broken membrane RO, seal vessel leak out 10: inproper sampling point,inproper dosage chemical,aluminium content make up; inproper quality conductivity feed RO, broken membrane RO, seal vessel leak out 11: inproper sampling point,chloride content make up high, less blowdown; inproper quality conductivity feed RO, broken membrane RO, seal vessel leak out 12: inproper sampling point,contamination,less blowdown; inproper quality conductivity feed RO, broken membrane RO, seal vessel leak out 13: inproper dosage chemical,contamination,less blowdown
[43 empty] | 131 | parameter CT boiler house | 1 | 2 | 1 | 2 | 3 | 4 | 5 | 6 | 7
| DEMIN TANK | [41 empty] | 132 | COOLING TOWER BOILER HOUSE | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | chloride | turbidity
| CONDENSATE TANK 200 | pH Tank 200 |  |  |  | #REF! | [36 empty] | 133 |  | no data | no data | no data | no data | no data | no data | no data | no data | no data
CONDENSATE TURBIN #3
| CONDENSATE MPS PP | [42 empty] | recommendation | 1: 1; 2: 2; 1: 3; 2: 4; no data 3: 5
| CONDENSATE LPS PP | [42 empty] | parameter RO | 1: pH; 2: Conductivity; 1: Total Hardness; 2: Silica; no data 3: Iron
| CONDENSATE MPS BH | [42 empty] | RO TANK | 1: please maintain; 2: please maintain; 1: please maintain; 2: please maintain; no data 3: please maintain
| CONDENSATE HPS BH | [42 empty] | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| CONDENSATE MPS GT | [42 empty] | parameter xi'an | inlet FRC | pH Feed a | Conduct feed a | FRC feed a | Turbidity feed a | pH Feed b | Conduct feed b | FRC feed b | turbidity feed b | pH permeate a | conduct permeate a | silica permeate a | pH permeate b | conduct permeate b | silica permeate b | pH mix a | conduct mix a | hard mix a | silica mix a | iron mix a | pH mix b | conduct mix b | hard mix b | silica mix b | iron mix b
| 0 | [42 empty] | RO XI'AN | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | no data | please maintain | please maintain | please maintain | keep quality pH permeate | keep quality conductivity permeate,check regeneration mixbed | check regeneration mixbed | check regeneration mixbed | check regeneration mixbed | keep quality pH permeate | keep quality conductivity permeate,check regeneration mixbed | check regeneration mixbed | check regeneration mixbed | check regeneration mixbed
| 0 | [42 empty] | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| 0 | [42 empty] | parameter yahua | inlet FRC | pH Feed | Conduct feed | FRC feed | Turbidity feed | pH permeate | conduct permeate | silica permeate | pH mix a | conduct mix a | hard mix a | silica mix a | iron mix a | pH mix b | conduct mix b | hard mix b | silica mix b | iron mix b
| 0 | [42 empty] | RO YAHUA | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | no data | keep quality pH permeate | keep quality conductivity permeate,check regeneration mixbed | check regeneration mixbed | check regeneration mixbed | check regeneration mixbed | keep quality pH permeate | keep quality conductivity permeate,check regeneration mixbed | check regeneration mixbed | check regeneration mixbed | check regeneration mixbed
| 0 | [42 empty] | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| 0 | [42 empty] | parameter jiangshu | inlet FRC | pH Feed a | Conduct feed a | FRC feed a | Turbidity feed a | pH Feed b | Conduct feed b | FRC feed b | turbidity feed b | pH permeate a | conduct permeate a | silica permeate a | pH permeate b | conduct permeate b | silica permeate b | pH mix a | conduct mix a | hard mix a | silica mix a | iron mix a | pH mix b | conduct mix b | hard mix b | silica mix b | iron mix b
| BOILER PP#1 | [42 empty] | RO JIANGSHU | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | keep quality pH permeate | keep quality conductivity permeate,check regeneration mixbed | check regeneration mixbed | check regeneration mixbed | check regeneration mixbed | keep quality pH permeate | keep quality conductivity permeate,check regeneration mixbed | check regeneration mixbed | check regeneration mixbed | check regeneration mixbed
| BOILER PP#2 | [42 empty] | 0: BUFFER DEMIN; 1: 1; 1: 2; 2: 3; 3: 4
| BOILER PP#3 | [42 empty] | 0: Parameter Demin Tank; 1: pH; 1: Conductivity; 2: Silica; 3: Iron
| BOILER PP#4 | [42 empty] | 0: DEMIN TANK; 1: please maintain; 1: please maintain; 2: please maintain; 3: keep quality permeate RO
| BOILER HP COAL | [42 empty] | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3
| BOILER HP GAS | [42 empty] | parameter dyn 1 | inlet FRC | pH Feed | Conduct feed | FRC feed | turbidity feed | pH permeate | conduct permeate | silica permeate
| BOILER MP | [42 empty] | RO DYNALON 1 | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain
| BOILER TOH #3 | [42 empty] | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3
| BOILER TOH #4 | [42 empty] | parameter dyn 2 | inlet FRC | pH Feed | Conduct feed | FRC feed | turbidity feed | pH permeate | conduct permeate | silica permeate
| BOILER HRSG #1 | [42 empty] | RO DYNALON 2 | please maintain | please maintain | please maintain | please maintain | please maintain | #NAME? | #NAME? | #NAME?
| BOILER HRSG #2 | [42 empty] | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 1 | 2 | 3 | 4 | 5
| BOILER OMNICAL | [42 empty] | parameter dyn 4 | inlet FRC | pH Feed | Conduct feed | FRC feed | turbidity feed | pH permeate | conduct permeate | silica permeate | pH mix | conduct mix | hard mix | silica mix | iron mix
| SWRO 1 | [42 empty] | RO DYNALON #4 | please maintain | please maintain | please maintain | please maintain | please maintain | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | please maintain
| SWRO 2 |  | Turbidity outlet DAF | Turbidity outlet DAF | Turbidity outlet DAF | Turbidity inlet MMF | [37 empty] | 0 | 1 | 1 | 2 | 3 | 4 | 1 | 2 | 3
| SWRO 3 |  |  |  |  | Turbidity inlet MMF | [9 empty] | conductivity Permeate 2 | [27 empty] | parameter new ro | inlet FRC | pH Feed | Conduct feed | FRC feed | turbidity feed | pH permeate | conduct permeate | silica permeate
| SWRO 4 | [42 empty] | NEW RO | stop | stop | stop | stop | stop | #NAME? | #NAME? | #NAME?
| PRODUCT SWRO |  | Conductivity Product SWRO #1 |  | Conductivity Product SWRO #5 | [38 empty] | 0: 0; 1: 1; 1: 2; 2: 3
| COOLING TOWER GT 1 | [42 empty] | 0: parameter domestic; 1: pH; 1: Conduct; 2: T.Hardness
| COOLING TOWER GT 2 | [42 empty] | 0: DOMESTIC TANK; 1: please maintain; 1: please maintain; 2: please maintain
| COOLING TOWER PP | [42 empty] | 0: parameter mixing; 1: pH; 1: Conduct; 2: T.Hardness
| COOLING TOWER COMPRESSOR | [42 empty] | 0: MIXING TANK; 1: please maintain; 1: please maintain; 2: please maintain
| COOLING TOWER BOILER HOUSE | [42 empty] | 0: parameter raw water; 1: pH; 1: Conduct; 2: T.Hardness
[44 empty] | RAW WATER TANK | please maintain | please maintain | please maintain
[44 empty] | parameter raw water | pH | Conduct | T.Hardness
[44 empty] | PDAM | please maintain | please maintain | please maintain
[44 empty] | 0 | 1 | 1 | 1 | 1 | 2
|  | RO WATER | Good Control | [40 empty] | parameter dyn 3 | FRC after biocide | FRC after 7408 | pH Feed | pH permeate | conduct permeate
|  | RO DEMIN | DEMIN TANK | [40 empty] | DYNALON #3 | no data | no data | no data | no data | no data
|  | RAW WATER | Good Control | [40 empty] | parameteer brine 1 | FRC after biocide | FRC after 7408 | pH Feed | pH permeate | conduct permeate
|  | FLOW STEAM | #REF! | [40 empty] | RO BRINE #1 | no data | no data | no data | no data | no data
|  | BOILER & BFW | Good Control | [40 empty] | parameter brine 2 | FRC after biocide | FRC after 7408 | pH Feed | pH permeate | conduct permeate
|  | SWRO | PRODUCT SWRO | [40 empty] | RO BRINE #2 | no data | no data | no data | no data | no data
|  | COOLING TOWER | Good Control | [40 empty] | parameter brine 3 | FRC after biocide | FRC after 7408 | pH Feed | pH permeate | conduct permeate
[44 empty] | RO Brine #3 | no data | no data | no data | no data | no data
[44 empty] | 0 | 1 | 2 | 3 | 4 | 5
[44 empty] | parameter demin tank | pH | Conductivity | Total Hardness | Silica | Iron
[44 empty] | DEMIN TANK | no data | no data | no data | no data | no data
[44 empty] | parameter condensate | pH | Conductivity | Total Hardness | Silica | Iron
[44 empty] | CONDENSATE TANK 200 | check injection point,check dosage chemical, check source water | please maintain | please maintain | please maintain | #REF!
[44 empty] | 0 | 1 | 2 | 3
[44 empty] | parameter steam | pH | Conductivity | Silica
[44 empty] | CONDENSATE TURBIN #3 | please maintain | please maintain | please maintain
| PLANT | BENCHMARK | COMPLIANCE | REMARKS |  |  | recom |  | RO WATER | RO DEMIN | RAW WATER | FLOW STEAM | BOILER & BFW | SWRO | COOLING TOWER | [28 empty] | 0: parameter steam; 1: pH; 2: Conductivity
| RO WATER | 100% | 100% |  |  |  | Please Maintain |  | 1 | 0.75 | 1 | #REF! | 1 | 0.5 | 1 | [28 empty] | 0: CONDENSATE MPS PP; 1: please maintain; 2: please maintain
|  |  |  | Good Control |  |  |  | Please Maintain |  | 0.75 |  | #REF! |  | 0.5 | [29 empty] | 0: parameter steam; 1: pH; 2: Conductivity
[44 empty] | CONDENSATE LPS PP | please maintain | please maintain
| RO DEMIN | 100% | 97.22% | Silica |  |  | check quality all mixbed & quality condensat water | [36 empty] | 0: parameter steam; 1: pH; 2: Conductivity
|  |  |  | DEMIN TANK | [15 empty] | 11 | 12 | 13 | 14 | 15 | 16 | 17 | [17 empty] | CONDENSATE MPS BH | stop | stop
|  |  |  | Out of Limit | [39 empty] | parameter steam | pH | Conductivity
| RAW WATER | 100% | 100% |  |  |  | Please Maintain | [36 empty] | CONDENSATE HPS BH | stop | stop
|  |  |  | Good Control | [39 empty] | parameter steam | pH | Conductivity
[27 empty] | 18 | [16 empty] | CONDENSATE MPS GT | stop | stop
| FLOW STEAM | 100% | #REF! | #REF! | [39 empty] | parameter MIXBED #1
|  |  |  | #REF! | [39 empty] | MIXBED #1
|  |  |  | #REF! | [39 empty] | parameter MIXBED #2
| BOILER & BFW | 100% | 97.7% |  |  |  | Please Maintain | [36 empty] | MIXBED #2
|  |  |  | Good Control | [39 empty] | parameter MIXBED #3
MIXBED #3
| SWRO | 100% | 82.5% | Conductivity Product SWRO #1 |  |  | keep quality conductivity permeate SWRO 1 | [36 empty] | parameter MIXBED #4
|  |  |  | PRODUCT SWRO | [39 empty] | MIXBED #4
|  |  |  | Out of Limit | [39 empty] | 0
| COOLING TOWER | 100% | 100% |  |  |  | Please Maintain | [36 empty] | 0
|  |  |  | Good Control | [39 empty] | 0
0
0
0
0
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | baris 1 | [16 empty] | 0
| RO WATER | [42 empty] | 0 | bar: baris 1
| RO DEMIN |  |  |  | Silica |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Silica | [16 empty] | 0
| RAW WATER | [42 empty] | 0 | bar: baris 1
| BOILER & BFW | [42 empty] | 0 | bar: baris 1
| SWRO | 2: Conductivity Product SWRO #1; 4: Conductivity Product SWRO #5; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; baris 1: Conductivity Product SWRO #1 | [16 empty] | 0
| COOLING TOWER | [42 empty] | parameter boiler high pressure | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4
[44 empty] | BOILER PP#1 | pH | Conductivity | T.Hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate
[44 empty] | parameter boiler high pressure | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | baris 1 | [16 empty] | BOILER PP#2 | pH | Conductivity | T.Hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate
| RO WATER | baris 1: Please Maintain | [16 empty] | parameter boiler high pressure | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain
| RO DEMIN |  |  |  | check quality all mixbed & quality condensat water |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | check quality all mixbed & quality condensat water | [16 empty] | BOILER PP#3 | pH | Conductivity | T.Hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate
| RAW WATER | baris 1: Please Maintain | [16 empty] | parameter boiler high pressure | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | stop | stop | stop | stop
| BOILER & BFW | baris 1: Please Maintain | [16 empty] | BOILER PP#4 | pH | Conductivity | T.Hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate
| SWRO | 2: keep quality conductivity permeate SWRO 1; 4: keep quality conductivity permeate SWRO 5; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; baris 1: keep quality conductivity permeate SWRO 1 | [16 empty] | parameter boiler high pressure | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain
| COOLING TOWER | baris 1: Please Maintain | [16 empty] | BOILER HP COAL | pH | Conductivity | T.Hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate
[44 empty] | parameter boiler high pressure | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
[44 empty] | BOILER HP GAS | pH | Conductivity | T.Hardness | Silica | Iron | Surgard | pH | Conductivity | Silica | Phosphate
| recommendation summary | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | [17 empty] | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
[44 empty] | parameter low pressure | 1 | 2 | 3 | 4 | 5 | 1 | 2 | 3 | 4 | 5 | 6
| RO TANK | [42 empty] | BOILER MP | pH | Conductivity | T.Hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite
| RO XI'AN | [42 empty] | parameter low pressure | stop | stop | no data | stop | stop | stop | stop | stop | stop | stop | stop
| RO YAHUA | [42 empty] | BOILER TOH #3 | pH | Conductivity | T.Hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite
| RO JIANGSHU | [42 empty] | parameter low pressure | please maintain | please maintain | please maintain | please maintain | please maintain | stop | stop | stop | stop | stop | stop
| Buffer Tank | [42 empty] | BOILER TOH #4 | pH | Conductivity | T.Hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite
| DEMIN TANK |  |  |  | check quality all mixbed & quality condensat water | [38 empty] | parameter low pressure | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain
| RO DYNALON 1 | [42 empty] | BOILER HRSG #1 | pH | Conductivity | T.Hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite
| RO DYNALON 2 | [5 empty] | #NAME? | #NAME? | #NAME? | [34 empty] | parameter low pressure | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
| RO DYNALON #4 | [5 empty] | #NAME? | #NAME? | #NAME? | [34 empty] | BOILER HRSG #2 | pH | Conductivity | T.Hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite
| NEW RO | [5 empty] | #NAME? | #NAME? | #NAME? | [34 empty] | parameter low pressure | stop | stop | stop | stop | no data | stop | stop | stop | stop | stop | stop
| MIXBED #1 | [42 empty] | BOILER OMNICAL | pH | Conductivity | T.Hardness | Silica | Iron | pH | Conductivity | O - Alkalinity | Silica | Phosphate | Sulphite
| MIXBED #2 | [42 empty] | 0 | please maintain | please maintain | please maintain | please maintain | no data | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain
| MIXBED #3 | [42 empty] | parameter sea water 1 | 1 | 1 | 2 | 3 | 1 | 1 | 2 | 1 | 1 | 2 | 3 | 1 | 2 | 1 | 2
| MIXBED #4 | [42 empty] | SWRO 1 | FRC | FRC | turbidity | turbidity | turbidity inlet mmf | iron outlet mmf | turbidity outlet mmf | pH feed | iron | FRC | turbidity | pH permeate a | Cond permeate a | pH permeate b | Cond permeate b
| DOMESTIC TANK | [42 empty] | 0 | stop | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | stop | stop | keep quality conductivity feed RO, check condition membrane RO, check condition seal vessel
| MIXING TANK | [42 empty] | parameter swro 2 | 1 | 1 | 2 | 3 | 4 | 1 | 1 | 2 | 1 | 1 | 2 | 3 | 1 | 2 | 1 | 2
| RAW WATER TANK | [42 empty] | SWRO 2 | FRC | FRC | turbidity | turbidity | turbidity | turbidity inlet mmf | iron outlet mmf | turbidity outlet mmf | pH feed | iron | FRC | turbidity | pH permeate a | Cond permeate a | pH permeate b | Cond permeate b
| PDAM | [42 empty] | parameter swro 3 | please maintain | check injection point, check injection line, adjust dosage | check injection point,adjust dosage,check operation DAF | check injection point,adjust dosage,check operation DAF | check injection point,adjust dosage,check operation DAF | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | keep quality conductivity feed RO, check condition membrane RO, check condition seal vessel
| DYNALON #3 | [42 empty] | SWRO 3 | FRC | FRC | turbidity | turbidity | turbidity | turbidity inlet mmf | iron outlet mmf | turbidity outlet mmf | pH feed | iron | FRC | turbidity | pH permeate a | Cond permeate a | pH permeate b | Cond permeate b
| RO BRINE #1 | [42 empty] | 0 | please maintain | #REF! | please maintain | please maintain | please maintain | keep quality turbidity outlet DAF, check dosage chemical | please maintain | please maintain | please maintain | please maintain | please maintain | please maintain | stop | stop | please maintain | keep quality conductivity feed RO, check condition membrane RO, check condition seal vessel
| RO BRINE #2 | [42 empty] | parameter swro 4 | 1: 1; 2: 1; 3: 2; 4: 3; 5: 1; 1: 2
| RO Brine #3 | [42 empty] | SWRO 4 | 1: pH feed; 2: iron; 3: FRC; 4: turbidity; 5: pH permeate a; 1: Cond permeate a
| DEMIN TANK | [42 empty] | 0 | 1: stop; 2: stop; 3: stop; 4: stop; 5: stop; 1: stop
| CONDENSATE TANK 200 | check injection point,check dosage chemical, check source water |  |  |  | #REF! | [37 empty] | parameter product swro | 1: 1; 2: 2; 3: 1; 4: 2
| CONDENSATE TURBIN #3 | [42 empty] | PRODUCT SWRO | 1: pH pro 1; 2: Cond pro 1; 3: pH pro 234; 4: Cond pro 234
| CONDENSATE MPS PP | [42 empty] | 0 | 1: please maintain; 2: keep quality conductivity permeate SWRO 1; 3: please maintain; 4: keep quality conductivity permeate SWRO 2,3 & 4
| CONDENSATE LPS PP | [42 empty] | parameter cooling tower | 1 | 2 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
| CONDENSATE MPS BH | [42 empty] | COOLING TOWER GT 1 | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | Zinc | Orthophosphate (filter) | Free Chlorine | Active Polymer | Aluminium | Chloride | Turbidity | TAB
| CONDENSATE HPS BH | [42 empty] | parameter cooling tower | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | check sampling point,check dosage chemical,check line chemical | check sampling point,control quality chloride make up,control continues blowdown | check sampling point,control quality make up,control continues blowdown | check dosage chemical,make sure not contaminated, control continues blowdown
| CONDENSATE MPS GT | [42 empty] | COOLING TOWER GT 2 | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | Zinc | Orthophosphate (filter) | Free Chlorine | Active Polymer | Aluminium | Chloride | Turbidity | TAB
| BOILER PP#1 | [42 empty] | parameter cooling tower | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | check sampling point,check dosage chemical,check line chemical | check sampling point,control quality chloride make up,control continues blowdown | check sampling point,control quality make up,control continues blowdown | check dosage chemical,make sure not contaminated, control continues blowdown
| BOILER PP#2 | [42 empty] | COOLING TOWER PP | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | Zinc | Orthophosphate (filter) | Free Chlorine | Active Polymer | Aluminium | Chloride | Turbidity | TAB
| BOILER PP#3 | [42 empty] | parameter cooling tower | please maintain | please maintain | please maintain | please maintain | no data | please maintain | no data | please maintain | please maintain | please maintain | please maintain | check sampling point,check dosage chemical,check line chemical | check sampling point,control quality chloride make up,control continues blowdown | check sampling point,control quality make up,control continues blowdown | check dosage chemical,make sure not contaminated, control continues blowdown
| BOILER PP#4 | [42 empty] | COOLING TOWER COMPRESSOR | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | Zinc | Orthophosphate (filter) | Free Chlorine | Active Polymer | Aluminium | Chloride | Turbidity | TAB
| BOILER HP COAL | [42 empty] | 0 | please maintain | please maintain | please maintain | please maintain | no data | please maintain | no data | please maintain | please maintain | please maintain | please maintain | check sampling point,check dosage chemical,check line chemical | check sampling point,control quality chloride make up,control continues blowdown | check sampling point,control quality make up,control continues blowdown | check dosage chemical,make sure not contaminated, control continues blowdown
| BOILER HP GAS | [42 empty] | parameter CT boiler house | 1 | 2 | 1 | 2 | 3 | 4 | 5 | 6 | 7
| BOILER MP | [42 empty] | COOLING TOWER BOILER HOUSE | pH MU | Cond MU | pH | Conductivity | Ca-Hardness | Iron | Silica | chloride | turbidity
| BOILER TOH #3 | [42 empty] | 0 | no data | no data | no data | no data | no data | no data | no data | no data | no data
BOILER TOH #4
BOILER HRSG #1
BOILER HRSG #2
BOILER OMNICAL
SWRO 1
| SWRO 2 |  | check injection point,adjust dosage,check operation DAF | check injection point,adjust dosage,check operation DAF | check injection point,adjust dosage,check operation DAF | keep quality turbidity outlet DAF, check dosage chemical | [9 empty] | keep quality conductivity feed RO, check condition membrane RO, check condition seal vessel
| SWRO 3 |  |  |  |  | keep quality turbidity outlet DAF, check dosage chemical | [9 empty] | keep quality conductivity feed RO, check condition membrane RO, check condition seal vessel
SWRO 4
| PRODUCT SWRO |  | keep quality conductivity permeate SWRO 1 |  | keep quality conductivity permeate SWRO 5
| COOLING TOWER GT 1 | [11 empty] | check sampling point,check dosage chemical,check line chemical | check sampling point,control quality chloride make up,control continues blowdown | check sampling point,control quality make up,control continues blowdown | check dosage chemical,make sure not contaminated, control continues blowdown
| COOLING TOWER GT 2 | [11 empty] | check sampling point,check dosage chemical,check line chemical | check sampling point,control quality chloride make up,control continues blowdown | check sampling point,control quality make up,control continues blowdown | check dosage chemical,make sure not contaminated, control continues blowdown
| COOLING TOWER PP | [11 empty] | check sampling point,check dosage chemical,check line chemical | check sampling point,control quality chloride make up,control continues blowdown | check sampling point,control quality make up,control continues blowdown | check dosage chemical,make sure not contaminated, control continues blowdown
| COOLING TOWER COMPRESSOR | [11 empty] | check sampling point,check dosage chemical,check line chemical | check sampling point,control quality chloride make up,control continues blowdown | check sampling point,control quality make up,control continues blowdown | check dosage chemical,make sure not contaminated, control continues blowdown
COOLING TOWER BOILER HOUSE
Note on AB545: diatur sesuai susunan yg lbih penting
Note on AB554: diatur sesuai susunan yg lbih penting

## RESUME
WATER ANALYSIS REPORT
DATE
DAILY COMPLIANCE |  |  | MTD COMPLIANCE
96.24% |  |  | 97.23%
PLANT | BENCHMARK | COMPLIANCE | REMARKS | RECOMMENDATION | SECTION |  |  |  | SUB SECTION
RO WATER | 100% | 100% |  | Please Maintain | SWRO 1 | stop
|  |  | Good Control |  | SWRO 2 | 86.21%
[5 empty] | SWRO 3 | 91.3%
DEMIN WATER | 100% | 97.22% | Silica | check quality all mixbed & quality condensat water | SWRO 4 | stop
|  |  | DEMIN TANK |  | PRODUCT SWRO | 70%
Out of Limit
RAW WATER | 100% | 100% |  | Please Maintain
Good Control
BOILER & BFW | 100% | 97.7% |  | Please Maintain
Good Control
SWRO | 100% | 82.5% | Conductivity Product SWRO #1 | keep quality conductivity permeate SWRO 1
PRODUCT SWRO
Out of Limit
COOLING TOWER | 100% | 100% |  | Please Maintain
Good Control
[7 empty] | PERFORMANCE | POTENTIAL PROBLEM |  | ROOT CAUSE | RECOMMENDATION
[5 empty] | FRC In DAF |  | FRC | 1 |  | 1 | 1
[5 empty] | turbidity |  | FRC | 1 |  | 1 | 1
[5 empty] | turbidity |  | turbidity | 2 |  | 2 | 2
[5 empty] | turbidity |  | turbidity | 3 |  | 3 | 3
[5 empty] | turbid in mmf |  | turbidity | 1 |  | 1 | 1
[5 empty] | iron out mmf |  | turbidity inlet mmf | 2 |  | 2 | 2
[5 empty] | turbidity out mmf |  | iron outlet mmf
[5 empty] | pH feed |  | turbidity outlet mmf
[5 empty] | iron |  | pH feed
[5 empty] | FRC |  | iron
[5 empty] | turbidity |  | FRC
[5 empty] | pH Perm a |  | turbidity
[5 empty] | Cond Perm a |  | pH perm a
[5 empty] | pH Perm b |  | Cond perm a
[5 empty] | Cond Perm b |  | pH perm b
Cond perm b

## RO WATER
| RO TANK 2000 MT | [6 empty] | RO #1A & #1B (XI'AN) | [19 empty] | RO #2 (YAHUA) | [10 empty] | RO #3A & #3B (JIANGSHU)
[8 empty] | INLET SAND FILTER | OUTLET SAND FILTER | FEED RO #1A |  |  |  | FEED RO #1B |  |  |  | PERMEATE RO #1A |  |  |  |  | PERMEATE RO #1B |  |  |  |  | INLET SAND FILTER | OUTLET SAND FILTER | FEED RO #2 |  |  |  | PERMEATE RO #2 |  |  |  |  | INLET SAND FILTER | OUTLET SAND FILTER | FEED RO #3A |  |  |  | FEED RO #3B |  |  |  | PERMEATE RO #3A |  |  |  |  | PERMEATE RO #3B
Date | pH | Conductivity | T. Hardness | Silica | Iron | Chloride | Turbidity | Free Chlorine | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Turbidity | pH | Conductivity | T. Hardness | Silica | Turbidity | Free Chlorine | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Turbidity | Free Chlorine | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Turbidity | pH | Conductivity | T. Hardness | Silica | Turbidity
|  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppmCl-) | NTU | (ppm Cl2) | NTU |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm SiO2) |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm SiO2) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm SiO2) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm SiO2) |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm SiO2)
| 5.0 - 7.0 | < 50 | 1.5; Max | < 5 | < 0.10 | < 30 | <1 | 0.20 - 0.50 | N/A | 6.0 - 6.5 | < 1000 | < 0.10 | < 0.50 | 6.0 - 6.5 | < 1000 | < 0.10 | < 0.50 | 5.0 - 7.0 | < 50 | 1.5 : Max | < 5 | < 1 | 5.0 - 7.0 | < 50 | 1.5 : Max | < 5 | < 1 | 0.20 - 0.50 | N/A | 6.0 - 6.5 | < 1000 | < 0.10 | < 0.50 | 5.0 - 7.0 | < 50 | 1.5 : Max | < 5 | < 1 | 0.20 - 0.50 | N/A | 6.0 - 6.5 | < 1000 | < 0.10 | < 0.50 | 6.0 - 6.5 | < 1000 | < 0.10 | < 0.50 | 5.0 - 7.0 | < 50 | 1.5 : Max | < 5 | < 1 | 5.0 - 7.0 | < 50 | 1.5 : Max | < 5 | < 1
Date
2026-09-01 | 5.85 | 37.8 | 0.74 | 1.355 | 0.05 | 10.24 | 0.83 | 0.4 | 0.54 | stop | stop | stop | stop | 6.41 | 685.7 | 0 | 0.35 | stop | stop | stop | stop | stop | 5.33 | 15.73 |  | 0.492 | 0.22 | 6.23 | 0.74 | 0.041 | 0.01 | 0.01 | 0.4 | stop | stop | stop | stop | stop | 0.36 | 0.38 | stop | stop | stop | stop | 6.5 | 738.8 | 0 | 0.18 | stop | stop | stop | stop | stop | 5.53 | 65.43 |  | 2.776 | 0.28
2026-09-02 | 5.62 | 41.86 | 0.59 | 1.15 | 0.04 | 10.57 | 0.31 | 0.24 | 0.25 | 6.23 | 647.2 | 0 | 0.22 | 6.25 | 644.9 | 0 | 0.29 | 5.29 | 21.86 |  | 0.496 | 0.28 | 5.29 | 21.86 |  | 0.496 | 0.28 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-03 | 5.82 | 30.2 | 0.337 | 0.738 | 0.04 | 9.95 | 0.44 | 0.28 | 0.3 | 6.46 | 644.3 | 0 | 0.19 | 6.49 | 641.3 | 0 | 0.2 | 5.39 | 19.7 |  | 0.475 | 0.32 | 5.38 | 15.41 |  | 0.37 | 0.37 | 0.24 | 0.4 | 6.5 | 654.7 | 0 | 0.26 | 5.45 | 19.71 |  | 0.487 | 0.3 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-04 | 5.94 | 39.02 | 0.54 | 1.152 | 0.04 | 10.12 | 0.35 | 0.24 | 0.22 | 6.46 | 597.6 | 0 | 0.16 | 6.5 | 596.1 | 0 | 0.2 | 5.38 | 19.82 |  | 0.701 | 0.31 | 5.37 | 15.62 |  | 0.475 | 0.27 | 0.42 | 0.48 | 6.48 | 606.3 | 0 | 0.3 | 5.31 | 22.9 |  | 0.724 | 0.23 | 0.28 | 0.21 | 6.5 | 562 | 0 | 0.33 | 6.48 | 564.2 | 0 | 0.3 | 5.38 | 23.41 |  | 0.773 | 0.26 | 5.48 | 49.54 |  | 2.218 | 0.18
2026-09-05 | 5.9 | 40.54 | 0.66 | 1.104 | 0.04 | 10.7 | 0.48 | 0.28 | 0.41 | 6.32 | 635.9 | 0 | 0.29 | 6.46 | 630.9 | 0 | 0.26 | 5.45 | 20.63 | 0.12 | 0.57 | 0.14 | 5.43 | 15.83 | 0.03 | 0.408 | 0.19 | 0.2 | 0.46 | 6.15 | 642.1 | 0 | 0.48 | 5.56 | 27.87 | 0.14 | 0.74 | 0.19 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-06 | 5.7 | 22.74 | 0.57 | 0.591 | 0.03 | 7.64 | 0.46
2026-09-07 | 5.7 | 36.68 | 0.62 | 1.17 | 0.02 | 10.46 | 0.28 | 0.35 | 0.38 | 6.4 | 540.4 | 0 | 0.24 | 6.44 | 538.9 | 0 | 0.25 | 5.12 | 18.25 |  | 0.701 | 0.44 | 5.18 | 14.35 |  | 0.544 | 0.39 | 0.24 | 0.37 | 6.28 | 532.1 | 0 | 0.24 | 5.09 | 20.69 |  | 1.109 | 0.45 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-08 | 5.69 | 32.6 | 0.52 | 0.884 | 0.02 | 9.2 | 0.69 | 0.25 | 0.43 | 6.39 | 587.3 | 0 | 0.26 | 6.4 | 586.4 | 0 | 0.28 | 5.17 | 21.03 |  | 0.753 | 0.23 | 5.28 | 16.72 |  | 0.555 | 0.24 | 0.5 | 0.55 | 6.45 | 616.9 | 0 | 0.31 | 5.34 | 26.3 |  | 1.088 | 0.27 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-09 | 5.62 | 27.96 | 0.59 | 0.92 | 0.02 | 8.44 | 0.28 | 0.3 | 0.39 | 6.21 | 618.9 | 0 | 0.27 | 6.32 | 633.8 | 0 | 0.25 | 5.2 | 23.3 |  | 0.706 | 0.28 | 5.24 | 19.59 |  | 0.527 | 0.26 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 0.23 | 0.31 | 6.45 | 695.8 | 0 | 0.31 | 6.43 | 586 | 0 | 0.36 | 5.4 | 25.31 |  | 0.919 | 0.22 | 5.51 | 28.9 |  | 0.193 | 0.3
2026-09-10 | 5.4 | 39.8 | 0.39 | 0.733 | 0.01 | 11.8 | 0.48 | 0.21 | 0.42 | 6.25 | 672.1 | 0 | 0.3 | 6.29 | 668.9 | 0 | 0.28 | 5.22 | 25.45 |  | 0.77 | 0.35 | 5.32 | 21.04 |  | 0.623 | 0.37 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 0.34 | 0.4 | 6.4 | 687.1 | 0 | 0.28 | 6.49 | 651.6 | 0 | 0.34 | 5.66 | 25.01 |  | 0.786 | 0.2 | 5.75 | 0.38 |  | 2.311 | 0.38
2026-09-11 | 5.72 | 33.28 | 0.66 | 0.9 | 0.02 | 10.85 | 0.41 | 0.3 | 0.23 | 6.37 | 622 | 0 | 0.24 | 6.39 | 609 | 0 | 0.31 | 5.44 | 18.72 |  | 0.755 | 0.3 | 5.31 | 17.85 |  | 0.58 | 0.32 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 0.5 | 0.39 | 6.44 | 552.6 | 0 | 0.26 | 6.47 | 550.3 | 0 | 0.24 | 5.58 | 22.89 |  | 0.623 | 0.27 | 5.02 | 47.9 |  | 2.054 | 0.25
2026-09-12 | 5.89 | 41.86 | 0.77 | 0.517 | 0.08 | 13.04 | 0.57 | 0.35 | 0.29 | 6.04 | 677.6 | 0 | 0.23 | 6.07 | 683.5 | 0 | 0.23 | 5.2 | 28.23 | 0.33 | 0.371 | 0.25 | 5.22 | 24.66 | 0.14 | 0.358 | 0.27 | 0.2 | 0.65 | 6.13 | 681.5 | 0 | 0.27 | 5.2 | 24.64 | 0.16 | 0.452 | 0.24 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-13 | 5.61 | 26.92 | 0.3 | 0.963 | 0.04 | 6.43 | 0.22
2026-09-14 | 5.47 | 27.83 | 0.32 | 0.826 | 0.05 | 6.12 | 0.27 | 0.2 | 0.39 | 6.36 | 548.5 | 0 | 0.3 | 6.4 | 548.7 | 0 | 0.29 | 5.11 | 20.55 |  | 0.256 | 0.29 | 5.13 | 17.14 |  | 0.263 | 0.33 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-15 | 5.56 | 49.97 | 0.67 | 0.82 | 0.05 | 5.88 | 0.32 | 0.27 | 0.34 | 6.32 | 812.8 | 0 | 0.27 | 6.44 | 813.1 | 0 | 0.39 | 5.22 | 33.83 |  | 0.462 | 0.36 | 5.26 | 27.82 |  | 0.268 | 0.28 | 0.38 | 0.56 | 6.5 | 796.8 | 0 | 0.39 | 5.59 | 29.48 |  | 0.576 | 0.3 | 0.4 | 0.51 | 6.4 | 796.7 | 0 | 0.34 | 6.41 | 788.6 | 0 | 0.44 | 5.26 | 29.46 |  | 0.225 | 0.27 | 5.41 | 43.52 |  | 0.561 | 0.32
2026-09-16 | 5.47 | 37.17 | 0.31 | 1.06 | 0.06 | 9.1 | 0.54 | 0.28 | 0.31 | 6.31 | 764.4 | 0 | 0.23 | 6.33 | 765.4 | 0 | 0.28 | 5.14 | 29.97 |  | 0.861 | 0.33 | 5.17 | 25.14 |  | 0.765 | 0.36 | 0.2 | 0.36 | 6.5 | 743.2 | 0 | 0.3 | 5.43 | 26.46 |  | 0.985 | 0.29 | 0.27 | 0.34 | 6.34 | 721.3 | 0 | 0.3 | 6.41 | 715 | 0 | 0.35 | 5.13 | 26.99 |  | 0.204 | 0.36 | 5.26 | 63.16 |  | 0.833 | 0.49
2026-09-17 | 5.84 | 52.48 | 0.76 | 1.057 | 0.04 | 7.11 | 0.45 | 0.31 | 0.44 | 6.48 | 1029 | 0 | 0.36 | 6.46 | 1034 | 0 | 0.35 | 5.6 | 42.39 |  | 0.333 | 0.27 | 5.54 | 36.02 |  | 0.274 | 0.28 | 0.27 | 0.41 | 6.7 | 1016 | 0 | 0.42 | 5.52 | 39.25 |  | 0.313 | 0.4 | 0.29 | 0.59 | 6.47 | 1188 | 0 | 0.31 | 6.48 | 1187 | 0 | 0.33 | 5.43 | 45.63 |  | 0.37 | 0.5 | 5.42 | 110.4 |  | 1.101 | 0.39
2026-09-18 | 5.53 | 45.04 | 0.44 | 0.85 | 0.07 | 17.38 | 0.45 | 0.5 | 0.41 | 6.23 | 1039 | 0 | 0.29 | 6.23 | 1034 | 0 | 0.41 | 5.22 | 44.19 |  | 0.237 | 0.56 | 5.3 | 38.22 |  | 0.231 | 0.27 | 0.27 | 0.99 | 6.28 | 1035 | 0 | 0.41 | 5.19 | 45.34 |  | 0.284 | 0.27 | 0.34 | 0.56 | 6.25 | 997.8 | 0 | 0.29 | stop | stop | stop | stop | 5.23 | 38.51 |  | 0.215 | 0.52 | stop | stop | stop | stop | stop
2026-09-19 | 5.86 | 36.91 | 0.38 | 0.858 | 0.04 | 13.97 | 0.16 | 0.5 | 0.18 | 6.31 | 912.6 | 0 | 0.2 | 6.46 | 912.1 | 0 | 0.22 | 5.58 | 35.68 | 0.38 | 0.92 | 0.1 | 5.41 | 31.45 | 0.2 | 0.761 | 0.2 | 0.28 | 0.33 | 6.49 | 915.1 | 0 | 0.17 | 5.34 | 34.4 | 0.39 | 0.875 | 0.27 | 0.5 | 0.31 | 6.36 | 913.5 | 0 | 0.16 | stop | stop | stop | stop | 5.32 | 33.18 | 0.24 | 0.624 | 0.17 | stop | stop | stop | stop | stop
2026-09-20 | 5.7 | 38.51 | 0.48 | 0.925 | 0.03 | 4.14 | 1.17
2026-09-21 | 5.88 | 49.43 | 0.51 | 0.75 | 0.03 | 12.12 | 0.53 | 0.37 | 0.43 | 6.36 | 899.3 | 0 | 0.42 | 6.45 | 888.7 | 0 | 0.31 | 5.43 | 36.66 |  | 0.847 | 0.28 | 5.4 | 34.22 |  | 0.812 | 0.25 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-22 | 5.95 | 49.78 | 0.84 | 0.795 | 0.04 | 11.23 | 0.78 | 0.44 | 0.3 | 6.33 | 747.3 | 0 | 0.15 | 6.33 | 747.3 | 0 | 0.17 | 5.36 | 30.25 |  | 0.559 | 0.29 | 5.4 | 28.44 |  | 0.469 | 0.3 | 0.3 | 0.35 | 6.4 | 733.4 | 0 | 0.23 | 5.75 | 26.88 |  | 0.69 | 0.28 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-23 | 5.93 | 58.28 | 0.99 | 0.941 | 0.03 | 14.41 | 0.8 | 0.14 | 0.58 | 6.22 | 1225 | 0 | 0.35 | 6.29 | 1236 | 0 | 0.25 | 5.41 | 52.28 |  | 0.602 | 0.37 | 5.36 | 49.98 |  | 0.663 | 0.5 | 0.5 | 0.85 | 6.5 | 1245 | 0 | 0.24 | 5.52 | 48.48 |  | 0.788 | 0.16 | 0.11 | 0.83 | 6.63 | 1251 | 0 | 0.21 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-24 | 5.91 | 36.03 | 0.56 | 0.991 | 0.02 | 10.34 | 0.53 | 0.06 | 0.42 | 6.07 | 829.3 | 0 | 0.25 | 6.15 | 832.7 | 0 | 0.3 | 5.37 | 35.1 |  | 0.95 | 0.28 | 5.32 | 35.29 |  | 0.987 | 0.33 | 0.45 | 0.4 | 6.31 | 829.2 | 0.01 | 0.3 | 5.42 | 33.33 |  | 0.731 | 0.35 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-25 | 5.96 | 39.98 | 0.9 | 0.576 | 0.03 | 12.53 | 0.59 | 0.47 | 0.81 | 6.38 | 798 | 0 | 0.48 | 6.38 | 801.1 | 0 | 0.49 | 5.51 | 33.58 |  | 0.408 | 0.4 | 5.45 | 34.65 |  | 0.477 | 0.45 | 0.5 | 0.51 | 6.43 | 809.3 | 0 | 0.46 | 5.48 | 34.36 |  | 0.318 | 0.45 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-26 | 5.76 | 29.06 | 0.4 | 0.757 | 0.02 | 8.13 | 0.3 | 0.2 | 0.51 | 6.45 | 997.8 | 0 | 0.28 | 6.12 | 948.5 | 0 | 0.25 | 5.42 | 41.43 | 0.9 | 0.576 | 0.31 | 5.47 | 27.02 | 0.09 | 0.599 | 0.5 | 0.5 | 0.29 | 6.44 | 993.1 | 0 | 0.28 | 5.34 | 46.75 | 0.62 | 1.033 | 0.23 | 0.2 | 0.39 | 6.61 | 453.2 | 0 | 0.17 | stop | stop | stop | stop | 5.5 | 15.1 | 0.14 | 0.557 | 0.28 | stop | stop | stop | stop | stop
2026-09-27 | 5.66 | 20.07 | 0.22 | 0.875 | 0.04 | 5.7 | 0.39
2026-09-28 | 5.62 | 26.71 | 0.38 | 0.78 | 0.03 | 6.91 | 0.43 | 0.5 | 0.41 | 6.46 | 983.1 | 0 | 0.26 | 6.5 | 981.2 | 0 | 0.23 | 5.36 | 40.96 |  | 1.124 | 0.24 | 5.48 | 25.1 |  | 0.689 | 0.32 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-29 | 5.85 | 33.95 | 0.36 | 0.901 | 0.06 | 8.25 | 0.48 | 0.3 | 0.45 | 6.26 | 906.1 | 0 | 0.28 | 6.44 | 906.8 | 0 | 0.35 | 5.77 | 39.06 |  | 0.958 | 0.28 | 5.7 | 23.39 |  | 0.579 | 0.24 | 0.2 | 0.59 | 6.39 | 932.1 | 0 | 0.35 | 5.48 | 45.64 |  | 1.246 | 0.23 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-30 | 5.89 | 30.22 | 0.25 | 0.94 | 0.05 | 7.83 | 0.39 | 0.28 | 0.39 | 6.48 | 785.9 | 0 | 0.34 | 6.5 | 784.5 | 0 | 0.35 | 5.48 | 32.64 |  | 1.187 | 0.22 | 5.51 | 20.12 |  | 0.69 | 0.45 | 0.21 | 0.59 | 6.16 | 821.3 | 0 | 0.4 | 5.63 | 40.85 |  | 1.367 | 0.3 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-10-01
| RO TANK 2000 MT | [6 empty] | RO #1A & #1B (XI'AN) | [19 empty] | RO #2 (YAHUA) | [10 empty] | RO #3A & #3B (JIANGSHU)
[8 empty] | INLET SAND FILTER | OUTLET SAND FILTER | FEED RO #1A |  |  |  | FEED RO #1B |  |  |  | PERMEATE RO #1A |  |  |  |  | PERMEATE RO #1B |  |  |  |  | INLET SAND FILTER | OUTLET SAND FILTER | FEED RO #2 |  |  |  | PERMEATE RO #2 |  |  |  |  | INLET SAND FILTER | OUTLET SAND FILTER | FEED RO #3A |  |  |  | FEED RO #3B |  |  |  | PERMEATE RO #3A |  |  |  |  | PERMEATE RO #3B
Date | pH | Conductivity | T. Hardness | Silica | Iron | Chloride | Turbidity | Free Chlorine | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Turbidity | pH | Conductivity | T. Hardness | Silica | Turbidity | Free Chlorine | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Turbidity | Free Chlorine | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Turbidity | pH | Conductivity | T. Hardness | Silica | Turbidity
|  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppmCl-) | NTU | (ppm Cl2) | NTU |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm SiO2) |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm SiO2) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm SiO2) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm SiO2) |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm SiO2)
| 5.0 - 7.0 | < 50 | 1.5; Max | < 5 | < 0.10 | < 30 | <1 | 0.20 - 0.50 | N/A | 6.0 - 6.5 | < 1000 | < 0.10 | < 0.50 | 6.0 - 6.5 | < 1000 | < 0.10 | < 0.50 | 5.0 - 7.0 | < 50 | 1.5 : Max | < 5 | < 1 | 5.0 - 7.0 | < 50 | 1.5 : Max | < 5 | < 1 | 0.20 - 0.50 | N/A | 6.0 - 6.5 | < 1000 | < 0.10 | < 0.50 | 5.0 - 7.0 | < 50 | 1.5 : Max | < 5 | < 1 | 0.20 - 0.50 | N/A | 6.0 - 6.5 | < 1000 | < 0.10 | < 0.50 | 6.0 - 6.5 | < 1000 | < 0.10 | < 0.50 | 5.0 - 7.0 | < 50 | 1.5 : Max | < 5 | < 1 | 5.0 - 7.0 | < 50 | 1.5 : Max | < 5 | < 1
2026-09-01 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-02 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-03 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-04 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100%
2026-09-05 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-06 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-07 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-08 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-09 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100%
2026-09-10 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100%
2026-09-11 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100%
2026-09-12 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-13 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-14 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-15 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100%
2026-09-16 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 0% | no data | 100% | 100%
2026-09-17 | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 0% | 0% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 0% | no data | 100% | 100%
2026-09-18 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | stop | stop | stop | stop | stop
2026-09-19 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop
2026-09-20 | 100% | 100% | 100% | 100% | 100% | 100% | 0% | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-21 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-22 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-23 | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 0% | 100% | 0% | 0% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-24 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-25 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-26 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop
2026-09-27 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-28 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-29 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-30 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-10-01 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
Conformance | 100% | 93.33% | 100% | 100% | 100% | 100% | 96.67% | 92.31% | 100% | 100% | 88.46% | 100% | 100% | 100% | 88.46% | 100% | 100% | 100% | 96.15% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 94.74% | 84.21% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 90.91% | 100% | 81.82% | 81.82% | 100% | 100% | 100% | 85.71% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 71.43% |  | 100% | 100%
OVERALL VALUE
Date | RO TANK | RO XI'AN | RO YAHUA | RO JIANGSHU
2026-09-01 | 100% | 100% | stop | stop
2026-09-02 | 100% | 100% | 100% | stop
2026-09-03 | 100% | 100% | 100% | stop
2026-09-04 | 100% | 100% | 100% | 100%
2026-09-05 | 100% | 100% | 100% | stop
2026-09-06 | 100% | no data | no data | no data
2026-09-07 | 100% | 100% | 100% | stop
2026-09-08 | 100% | 100% | 100% | stop
2026-09-09 | 100% | 100% | stop | 100%
2026-09-10 | 100% | 100% | stop | 100%
2026-09-11 | 100% | 100% | stop | 100%
2026-09-12 | 100% | 100% | 100% | stop
2026-09-13 | 100% | no data | no data | no data
2026-09-14 | 100% | 100% | stop | stop
2026-09-15 | 100% | 100% | 100% | 100%
2026-09-16 | 100% | 100% | 100% | 94.44%
2026-09-17 | 85.71% | 88.89% | 80% | 83.33%
2026-09-18 | 100% | 88.89% | 90% | 100%
2026-09-19 | 100% | 100% | 100% | 100%
2026-09-20 | 85.71% | no data | no data | no data
2026-09-21 | 100% | 100% | stop | stop
2026-09-22 | 100% | 100% | 100% | stop
2026-09-23 | 85.71% | 77.78% | 90% | 50%
2026-09-24 | 100% | 94.44% | 100% | stop
2026-09-25 | 100% | 100% | 100% | stop
2026-09-26 | 100% | 100% | 100% | 90.91%
2026-09-27 | 100% | no data | no data | no data
2026-09-28 | 100% | 100% | stop | stop
2026-09-29 | 100% | 100% | 100% | stop
2026-09-30 | 100% | 100% | 100% | stop
2026-10-01 | no data | no data | no data | no data
Conformance | 98.57% | 98.08% | 97.89% | 92.61%
RO & MIXBED
2026-09-01 | 100%
2026-09-02 | 100%
2026-09-03 | 100%
2026-09-04 | 100%
2026-09-05 | 100%
2026-09-06 | 100%
2026-09-07 | 100%
2026-09-08 | 100%
2026-09-09 | 100%
2026-09-10 | 100%
2026-09-11 | 100%
2026-09-12 | 100%
2026-09-13 | 100%
2026-09-14 | 100%
2026-09-15 | 100%
2026-09-16 | 98.61%
2026-09-17 | 84.48%
2026-09-18 | 94.72%
2026-09-19 | 100%
2026-09-20 | 85.71%
2026-09-21 | 100%
2026-09-22 | 100%
2026-09-23 | 75.87%
2026-09-24 | 98.15%
2026-09-25 | 100%
2026-09-26 | 97.73%
2026-09-27 | 100%
2026-09-28 | 100%
2026-09-29 | 100%
2026-09-30 | 100%
2026-10-01
Note on I30: dosing pump NaOCl trouble
Note on I31: dosing pump NaOCl trouble

## FLOW STEAM (hidden)
BOILER POWER PLANT | [5 empty] | BOILER POWER PLANT |  |  |  |  | BOILER POWER PLANT |  |  |  |  | BOILER POWER PLANT |  |  |  |  | BOILER HP |  |  |  |  | BOILER HP |  |  |  |  | BOILER YAHUA MP |  |  |  |  | BOILER HRSG TOH |  |  |  |  | BOILER HRSG TOH |  |  |  |  | BOILER HRSG GAS TURBIN |  |  |  |  | BOILER HRSG GAS TURBIN
BOILER PP #1 | [5 empty] | BOILER PP #2 |  |  |  |  | BOILER PP #3 |  |  |  |  | BOILER PP #4 |  |  |  |  | BOILER HP COAL |  |  |  |  | BOILER HP GAS |  |  |  |  | BOILER MP |  |  |  |  | BOILER TOH #3 |  |  |  |  | BOILER TOH #4 |  |  |  |  | BOILER HRSG GT #1 |  |  |  |  | BOILER HRSG GT #2
Date | Temperature Deaerator | Tekanan Operasi Boiler | Steam Flow Rate | Feed Water Flow Rate | Feed Water Temperature | Temperature Deaerator | Tekanan Operasi Boiler | Steam Flow Rate | Feed Water Flow Rate | Feed Water Temperature | Temperature Deaerator | Tekanan Operasi Boiler | Steam Flow Rate | Feed Water Flow Rate | Feed Water Temperature | Temperature Deaerator | Tekanan Operasi Boiler | Steam Flow Rate | Feed Water Flow Rate | Feed Water Temperature | Temperature Deaerator | Tekanan Operasi Boiler | Steam Flow Rate | Feed Water Flow Rate | Feed Water Temperature | Temperature Deaerator | Tekanan Operasi Boiler | Steam Flow Rate | Feed Water Flow Rate | Feed Water Temperature | Temperature Deaerator | Tekanan Operasi Boiler | Steam Flow Rate | Feed Water Flow Rate | Feed Water Temperature | Temperature Deaerator | Tekanan Operasi Boiler | Steam Flow Rate | Feed Water Flow Rate | Feed Water Temperature | Temperature Deaerator | Tekanan Operasi Boiler | Steam Flow Rate | Feed Water Flow Rate | Feed Water Temperature | Temperature Deaerator | Tekanan Operasi Boiler | Steam Flow Rate | Feed Water Flow Rate | Feed Water Temperature | Temperature Deaerator | Tekanan Operasi Boiler | Steam Flow Rate | Feed Water Flow Rate | Feed Water Temperature
| oC ( MIN 100 oC ) | kg/cm2 | m3/h | m3/h | oC | oC ( MIN 100 oC ) | kg/cm2 | m3/h | m3/h | oC | oC ( MIN 100 oC ) | kg/cm2 | m3/h | m3/h | oC | oC ( MIN 100 oC ) | kg/cm2 | m3/h | m3/h | oC | oC ( MIN 100 oC ) | kg/cm2 | m3/h | m3/h | oC | oC ( MIN 100 oC ) | kg/cm2 | m3/h | m3/h | oC | oC ( MIN 100 oC ) | kg/cm2 | m3/h | m3/h | oC | oC ( MIN 100 oC ) | kg/cm2 | m3/h | m3/h | oC | oC ( MIN 100 oC ) | kg/cm2 | m3/h | m3/h | oC | oC ( MIN 100 oC ) | kg/cm2 | m3/h | m3/h | oC | oC ( MIN 100 oC ) | kg/cm2 | m3/h | m3/h | oC
2020-05-01 | 102 | 43.1 | 68.3 | 50.2 |  | 102 | 43.1 | 68.3 | 50.2 |  | 102 | 43.1 | 68.3 | 50.2 |  | 102 | 43.1 | 68.3 | 50.2 |  | 102 | 43.1 | 68.3 | 50.2 | 102.1 | 102 | 43.1 | 68.3 | 50.2 | 102.1 | 102 | 43.1 | 68.3 | 50.2 | 102.1 | 102 | 43.1 | 68.3 | 50.2 |  | 102 | 43.1 | 68.3 | 50.2 |  | 102 | 43.1 | 68.3 | 50.2 |  | 102 | 43.1 | 68.3 | 50.2
2020-05-02 | 102.1 | 44.2 | 69.5 | 54.2 |  | 102.1 | 44.2 | 69.5 | 54.2 |  | 102.1 | 44.2 | 69.5 | 54.2 |  | 102.1 | 44.2 | 69.5 | 54.2 |  | 102.1 | 44.2 | 69.5 | 54.2 | 102.3 | 102.1 | 44.2 | 69.5 | 54.2 | 102.3 | 102.1 | 44.2 | 69.5 | 54.2 | 102.3 | 102.1 | 44.2 | 69.5 | 54.2 |  | 102.1 | 44.2 | 69.5 | 54.2 |  | 102.1 | 44.2 | 69.5 | 54.2 |  | 102.1 | 44.2 | 69.5 | 54.2
2020-05-03 | 103.6 | 43.2 | 55.3 | 67.2 |  | 103.6 | 43.2 | 55.3 | 67.2 |  | 103.6 | 43.2 | 55.3 | 67.2 |  | 103.6 | 43.2 | 55.3 | 67.2 |  | 103.6 | 43.2 | 55.3 | 67.2 | 101.8 | 103.6 | 43.2 | 55.3 | 67.2 | 101.8 | 103.6 | 43.2 | 55.3 | 67.2 | 101.8 | 103.6 | 43.2 | 55.3 | 67.2 |  | 103.6 | 43.2 | 55.3 | 67.2 |  | 103.6 | 43.2 | 55.3 | 67.2 |  | 103.6 | 43.2 | 55.3 | 67.2
2020-05-04 | 105.2 | 44.3 | 65.1 | 60.1 |  | 105.2 | 44.3 | 65.1 | 60.1 |  | 105.2 | 44.3 | 65.1 | 60.1 |  | 105.2 | 44.3 | 65.1 | 60.1 |  | 105.2 | 44.3 | 65.1 | 60.1 | 101 | 105.2 | 44.3 | 65.1 | 60.1 | 101 | 105.2 | 44.3 | 65.1 | 60.1 | 101 | 105.2 | 44.3 | 65.1 | 60.1 |  | 105.2 | 44.3 | 65.1 | 60.1 |  | 105.2 | 44.3 | 65.1 | 60.1 |  | 105.2 | 44.3 | 65.1 | 60.1
2020-05-05 | 105.2 | 45.2 | 59.3 | 41.3 |  | 105.2 | 45.2 | 59.3 | 41.3 |  | 105.2 | 45.2 | 59.3 | 41.3 |  | 105.2 | 45.2 | 59.3 | 41.3 |  | 105.2 | 45.2 | 59.3 | 41.3 | 101 | 105.2 | 45.2 | 59.3 | 41.3 | 101 | 105.2 | 45.2 | 59.3 | 41.3 | 101 | 105.2 | 45.2 | 59.3 | 41.3 |  | 105.2 | 45.2 | 59.3 | 41.3 |  | 105.2 | 45.2 | 59.3 | 41.3 |  | 105.2 | 45.2 | 59.3 | 41.3
2020-05-06 | 102.3 | 44.1 | 62.3 | 49.3 |  | 102.3 | 44.1 | 62.3 | 49.3 |  | 102.3 | 44.1 | 62.3 | 49.3 |  | 102.3 | 44.1 | 62.3 | 49.3 |  | 102.3 | 44.1 | 62.3 | 49.3 | 101 | 102.3 | 44.1 | 62.3 | 49.3 | 101 | 102.3 | 44.1 | 62.3 | 49.3 | 101 | 102.3 | 44.1 | 62.3 | 49.3 |  | 102.3 | 44.1 | 62.3 | 49.3 |  | 102.3 | 44.1 | 62.3 | 49.3 |  | 102.3 | 44.1 | 62.3 | 49.3
2020-05-07 | 102.3 | 43 | 62.8 | 45 |  | 102.3 | 43 | 62.8 | 45 |  | 102.3 | 43 | 62.8 | 45 |  | 102.3 | 43 | 62.8 | 45 |  | 102.3 | 43 | 62.8 | 45 | 101 | 102.3 | 43 | 62.8 | 45 | 101 | 102.3 | 43 | 62.8 | 45 | 101 | 102.3 | 43 | 62.8 | 45 |  | 102.3 | 43 | 62.8 | 45 |  | 102.3 | 43 | 62.8 | 45 |  | 102.3 | 43 | 62.8 | 45
2020-05-08 | 102.2 | 46.2 | 56.1 | 52.3 |  | 102.2 | 46.2 | 56.1 | 52.3 |  | 102.2 | 46.2 | 56.1 | 52.3 |  | 102.2 | 46.2 | 56.1 | 52.3 |  | 102.2 | 46.2 | 56.1 | 52.3 | 101 | 102.2 | 46.2 | 56.1 | 52.3 | 101 | 102.2 | 46.2 | 56.1 | 52.3 | 101 | 102.2 | 46.2 | 56.1 | 52.3 |  | 102.2 | 46.2 | 56.1 | 52.3 |  | 102.2 | 46.2 | 56.1 | 52.3 |  | 102.2 | 46.2 | 56.1 | 52.3
2020-05-09 | 101.3 | 44.2 | 62.1 | 42.3 |  | 101.3 | 44.2 | 62.1 | 42.3 |  | 101.3 | 44.2 | 62.1 | 42.3 |  | 101.3 | 44.2 | 62.1 | 42.3 |  | 101.3 | 44.2 | 62.1 | 42.3 | 100 | 101.3 | 44.2 | 62.1 | 42.3 | 100 | 101.3 | 44.2 | 62.1 | 42.3 | 100 | 101.3 | 44.2 | 62.1 | 42.3 |  | 101.3 | 44.2 | 62.1 | 42.3 |  | 101.3 | 44.2 | 62.1 | 42.3 |  | 101.3 | 44.2 | 62.1 | 42.3
2020-05-10 | 102.1 | 45.4 | 60.2 | 54.1 |  | 102.1 | 45.4 | 60.2 | 54.1 |  | 102.1 | 45.4 | 60.2 | 54.1 |  | 102.1 | 45.4 | 60.2 | 54.1 |  | 102.1 | 45.4 | 60.2 | 54.1 | 99.3 | 102.1 | 45.4 | 60.2 | 54.1 | 99.3 | 102.1 | 45.4 | 60.2 | 54.1 | 99.3 | 102.1 | 45.4 | 60.2 | 54.1 |  | 102.1 | 45.4 | 60.2 | 54.1 |  | 102.1 | 45.4 | 60.2 | 54.1 |  | 102.1 | 45.4 | 60.2 | 54.1
2020-05-11 | 102.2 | 45.3 | 62.1 | 41.3 |  | 102.2 | 45.3 | 62.1 | 41.3 |  | 102.2 | 45.3 | 62.1 | 41.3 |  | 102.2 | 45.3 | 62.1 | 41.3 |  | 102.2 | 45.3 | 62.1 | 41.3 | 100 | 102.2 | 45.3 | 62.1 | 41.3 | 100 | 102.2 | 45.3 | 62.1 | 41.3 | 100 | 102.2 | 45.3 | 62.1 | 41.3 |  | 102.2 | 45.3 | 62.1 | 41.3 |  | 102.2 | 45.3 | 62.1 | 41.3 |  | 102.2 | 45.3 | 62.1 | 41.3
2020-05-12 | 102.1 | 44.3 | 60.3 | 42.3 |  | 102.1 | 44.3 | 60.3 | 42.3 |  | 102.1 | 44.3 | 60.3 | 42.3 |  | 102.1 | 44.3 | 60.3 | 42.3 |  | 102.1 | 44.3 | 60.3 | 42.3 | 101 | 102.1 | 44.3 | 60.3 | 42.3 | 101 | 102.1 | 44.3 | 60.3 | 42.3 | 101 | 102.1 | 44.3 | 60.3 | 42.3 |  | 102.1 | 44.3 | 60.3 | 42.3 |  | 102.1 | 44.3 | 60.3 | 42.3 |  | 102.1 | 44.3 | 60.3 | 42.3
2020-05-13 | 103.1 | 45.2 | 62.2 | 43.2 |  | 103.1 | 45.2 | 62.2 | 43.2 |  | 103.1 | 45.2 | 62.2 | 43.2 |  | 103.1 | 45.2 | 62.2 | 43.2 |  | 103.1 | 45.2 | 62.2 | 43.2 | 101.3 | 103.1 | 45.2 | 62.2 | 43.2 | 101.3 | 103.1 | 45.2 | 62.2 | 43.2 | 101.3 | 103.1 | 45.2 | 62.2 | 43.2 |  | 103.1 | 45.2 | 62.2 | 43.2 |  | 103.1 | 45.2 | 62.2 | 43.2 |  | 103.1 | 45.2 | 62.2 | 43.2
2020-05-14 | 103.1 | 44.1 | 60.3 | 42.1 |  | 103.1 | 44.1 | 60.3 | 42.1 |  | 103.1 | 44.1 | 60.3 | 42.1 |  | 103.1 | 44.1 | 60.3 | 42.1 |  | 103.1 | 44.1 | 60.3 | 42.1 | 101.7 | 103.1 | 44.1 | 60.3 | 42.1 | 101.7 | 103.1 | 44.1 | 60.3 | 42.1 | 101.7 | 103.1 | 44.1 | 60.3 | 42.1 |  | 103.1 | 44.1 | 60.3 | 42.1 |  | 103.1 | 44.1 | 60.3 | 42.1 |  | 103.1 | 44.1 | 60.3 | 42.1
2020-05-15 | 103.2 | 44.3 | 62.1 | 49.3 |  | 103.2 | 44.3 | 62.1 | 49.3 |  | 103.2 | 44.3 | 62.1 | 49.3 |  | 103.2 | 44.3 | 62.1 | 49.3 |  | 103.2 | 44.3 | 62.1 | 49.3 | 101.1 | 103.2 | 44.3 | 62.1 | 49.3 | 101.1 | 103.2 | 44.3 | 62.1 | 49.3 | 101.1 | 103.2 | 44.3 | 62.1 | 49.3 |  | 103.2 | 44.3 | 62.1 | 49.3 |  | 103.2 | 44.3 | 62.1 | 49.3 |  | 103.2 | 44.3 | 62.1 | 49.3
2020-05-16 | 103.3 | 45.2 | 62.3 | 43.4 |  | 103.3 | 45.2 | 62.3 | 43.4 |  | 103.3 | 45.2 | 62.3 | 43.4 |  | 103.3 | 45.2 | 62.3 | 43.4 |  | 103.3 | 45.2 | 62.3 | 43.4 | 102.1 | 103.3 | 45.2 | 62.3 | 43.4 | 102.1 | 103.3 | 45.2 | 62.3 | 43.4 | 102.1 | 103.3 | 45.2 | 62.3 | 43.4 |  | 103.3 | 45.2 | 62.3 | 43.4 |  | 103.3 | 45.2 | 62.3 | 43.4 |  | 103.3 | 45.2 | 62.3 | 43.4
2020-05-17 | 103.6 | 44.7 | 48.5 | 64.9 |  | 103.6 | 44.7 | 48.5 | 64.9 |  | 103.6 | 44.7 | 48.5 | 64.9 |  | 103.6 | 44.7 | 48.5 | 64.9 |  | 103.6 | 44.7 | 48.5 | 64.9 | 101.3 | 103.6 | 44.7 | 48.5 | 64.9 | 101.3 | 103.6 | 44.7 | 48.5 | 64.9 | 101.3 | 103.6 | 44.7 | 48.5 | 64.9 |  | 103.6 | 44.7 | 48.5 | 64.9 |  | 103.6 | 44.7 | 48.5 | 64.9 |  | 103.6 | 44.7 | 48.5 | 64.9
2020-05-18 | 102.1 | 45.3 | 58.2 | 47.1 |  | 102.1 | 45.3 | 58.2 | 47.1 |  | 102.1 | 45.3 | 58.2 | 47.1 |  | 102.1 | 45.3 | 58.2 | 47.1 |  | 102.1 | 45.3 | 58.2 | 47.1 | 101 | 102.1 | 45.3 | 58.2 | 47.1 | 101 | 102.1 | 45.3 | 58.2 | 47.1 | 101 | 102.1 | 45.3 | 58.2 | 47.1 |  | 102.1 | 45.3 | 58.2 | 47.1 |  | 102.1 | 45.3 | 58.2 | 47.1 |  | 102.1 | 45.3 | 58.2 | 47.1
2020-05-19 | 103.2 | 44.1 | 62.3 | 44.3 |  | 103.2 | 44.1 | 62.3 | 44.3 |  | 103.2 | 44.1 | 62.3 | 44.3 |  | 103.2 | 44.1 | 62.3 | 44.3 |  | 103.2 | 44.1 | 62.3 | 44.3 | 101 | 103.2 | 44.1 | 62.3 | 44.3 | 101 | 103.2 | 44.1 | 62.3 | 44.3 | 101 | 103.2 | 44.1 | 62.3 | 44.3 |  | 103.2 | 44.1 | 62.3 | 44.3 |  | 103.2 | 44.1 | 62.3 | 44.3 |  | 103.2 | 44.1 | 62.3 | 44.3
2020-05-20 | 103 | 45.1 | 56.2 | 42.1 |  | 103 | 45.1 | 56.2 | 42.1 |  | 103 | 45.1 | 56.2 | 42.1 |  | 103 | 45.1 | 56.2 | 42.1 |  | 103 | 45.1 | 56.2 | 42.1 | 101 | 103 | 45.1 | 56.2 | 42.1 | 101 | 103 | 45.1 | 56.2 | 42.1 | 101 | 103 | 45.1 | 56.2 | 42.1 |  | 103 | 45.1 | 56.2 | 42.1 |  | 103 | 45.1 | 56.2 | 42.1 |  | 103 | 45.1 | 56.2 | 42.1
2020-05-21 | 102.7 | 40.1 | 52.3 | 38.6 |  | 102.7 | 40.1 | 52.3 | 38.6 |  | 102.7 | 40.1 | 52.3 | 38.6 |  | 102.7 | 40.1 | 52.3 | 38.6 |  | 102.7 | 40.1 | 52.3 | 38.6 | 101.2 | 102.7 | 40.1 | 52.3 | 38.6 | 101.2 | 102.7 | 40.1 | 52.3 | 38.6 | 101.2 | 102.7 | 40.1 | 52.3 | 38.6 |  | 102.7 | 40.1 | 52.3 | 38.6 |  | 102.7 | 40.1 | 52.3 | 38.6 |  | 102.7 | 40.1 | 52.3 | 38.6
2020-05-22 | 102.1 | 43.3 | 58.1 | 45.1 |  | 102.1 | 43.3 | 58.1 | 45.1 |  | 102.1 | 43.3 | 58.1 | 45.1 |  | 102.1 | 43.3 | 58.1 | 45.1 |  | 102.1 | 43.3 | 58.1 | 45.1 | 100.6 | 102.1 | 43.3 | 58.1 | 45.1 | 100.6 | 102.1 | 43.3 | 58.1 | 45.1 | 100.6 | 102.1 | 43.3 | 58.1 | 45.1 |  | 102.1 | 43.3 | 58.1 | 45.1 |  | 102.1 | 43.3 | 58.1 | 45.1 |  | 102.1 | 43.3 | 58.1 | 45.1
2020-05-23 | off | 46.3 | 55.3 | 46.2 |  | off | 46.3 | 55.3 | 46.2 |  | off | 46.3 | 55.3 | 46.2 |  | off | 46.3 | 55.3 | 46.2 |  | off | 46.3 | 55.3 | 46.2 | 101.1 | off | 46.3 | 55.3 | 46.2 | 101.1 | off | 46.3 | 55.3 | 46.2 | 101.1 | off | 46.3 | 55.3 | 46.2 |  | off | 46.3 | 55.3 | 46.2 |  | off | 46.3 | 55.3 | 46.2 |  | off | 46.3 | 55.3 | 46.2
2020-05-24 | 105.2 | 45.3 | 63.1 | 57.4 |  | 105.2 | 45.3 | 63.1 | 57.4 |  | 105.2 | 45.3 | 63.1 | 57.4 |  | 105.2 | 45.3 | 63.1 | 57.4 |  | 105.2 | 45.3 | 63.1 | 57.4 | 100.1 | 105.2 | 45.3 | 63.1 | 57.4 | 100.1 | 105.2 | 45.3 | 63.1 | 57.4 | 100.1 | 105.2 | 45.3 | 63.1 | 57.4 |  | 105.2 | 45.3 | 63.1 | 57.4 |  | 105.2 | 45.3 | 63.1 | 57.4 |  | 105.2 | 45.3 | 63.1 | 57.4
2020-05-25 | 102.6 | 45.8 | 45.9 | 63.1 |  | 102.6 | 45.8 | 45.9 | 63.1 |  | 102.6 | 45.8 | 45.9 | 63.1 |  | 102.6 | 45.8 | 45.9 | 63.1 |  | 102.6 | 45.8 | 45.9 | 63.1 | 100.2 | 102.6 | 45.8 | 45.9 | 63.1 | 100.2 | 102.6 | 45.8 | 45.9 | 63.1 | 100.2 | 102.6 | 45.8 | 45.9 | 63.1 |  | 102.6 | 45.8 | 45.9 | 63.1 |  | 102.6 | 45.8 | 45.9 | 63.1 |  | 102.6 | 45.8 | 45.9 | 63.1
2020-05-26 | 101.5 | 44.6 | 45.5 | 62.2 |  | 101.5 | 44.6 | 45.5 | 62.2 |  | 101.5 | 44.6 | 45.5 | 62.2 |  | 101.5 | 44.6 | 45.5 | 62.2 |  | 101.5 | 44.6 | 45.5 | 62.2 | 100.8 | 101.5 | 44.6 | 45.5 | 62.2 | 100.8 | 101.5 | 44.6 | 45.5 | 62.2 | 100.8 | 101.5 | 44.6 | 45.5 | 62.2 |  | 101.5 | 44.6 | 45.5 | 62.2 |  | 101.5 | 44.6 | 45.5 | 62.2 |  | 101.5 | 44.6 | 45.5 | 62.2
2020-05-27 | 102.4 | 43.1 | 42.2 | 61 |  | 102.4 | 43.1 | 42.2 | 61 |  | 102.4 | 43.1 | 42.2 | 61 |  | 102.4 | 43.1 | 42.2 | 61 |  | 102.4 | 43.1 | 42.2 | 61 | 101.3 | 102.4 | 43.1 | 42.2 | 61 | 101.3 | 102.4 | 43.1 | 42.2 | 61 | 101.3 | 102.4 | 43.1 | 42.2 | 61 |  | 102.4 | 43.1 | 42.2 | 61 |  | 102.4 | 43.1 | 42.2 | 61 |  | 102.4 | 43.1 | 42.2 | 61
2020-05-28 | 103.3 | 45.2 | 52.1 | 45.1 |  | 103.3 | 45.2 | 52.1 | 45.1 |  | 103.3 | 45.2 | 52.1 | 45.1 |  | 103.3 | 45.2 | 52.1 | 45.1 |  | 103.3 | 45.2 | 52.1 | 45.1 | 101.3 | 103.3 | 45.2 | 52.1 | 45.1 | 101.3 | 103.3 | 45.2 | 52.1 | 45.1 | 101.3 | 103.3 | 45.2 | 52.1 | 45.1 |  | 103.3 | 45.2 | 52.1 | 45.1 |  | 103.3 | 45.2 | 52.1 | 45.1 |  | 103.3 | 45.2 | 52.1 | 45.1
2020-05-29 | 103.5 | 45.3 | 58.1 | 42.1 |  | 103.5 | 45.3 | 58.1 | 42.1 |  | 103.5 | 45.3 | 58.1 | 42.1 |  | 103.5 | 45.3 | 58.1 | 42.1 |  | 103.5 | 45.3 | 58.1 | 42.1 | 103.2 | 103.5 | 45.3 | 58.1 | 42.1 | 103.2 | 103.5 | 45.3 | 58.1 | 42.1 | 103.2 | 103.5 | 45.3 | 58.1 | 42.1 |  | 103.5 | 45.3 | 58.1 | 42.1 |  | 103.5 | 45.3 | 58.1 | 42.1 |  | 103.5 | 45.3 | 58.1 | 42.1
2020-05-30 | 103.4 | 43.6 | 56.3 | 45.1 |  | 103.4 | 43.6 | 56.3 | 45.1 |  | 103.4 | 43.6 | 56.3 | 45.1 |  | 103.4 | 43.6 | 56.3 | 45.1 |  | 103.4 | 43.6 | 56.3 | 45.1 | 103.3 | 103.4 | 43.6 | 56.3 | 45.1 | 103.3 | 103.4 | 43.6 | 56.3 | 45.1 | 103.3 | 103.4 | 43.6 | 56.3 | 45.1 |  | 103.4 | 43.6 | 56.3 | 45.1 |  | 103.4 | 43.6 | 56.3 | 45.1 |  | 103.4 | 43.6 | 56.3 | 45.1
2020-05-31
BOILER POWER PLANT | [5 empty] | BOILER POWER PLANT |  |  |  |  | BOILER POWER PLANT |  |  |  |  | BOILER POWER PLANT |  |  |  |  | BOILER HP |  |  |  |  | BOILER HP |  |  |  |  | BOILER YAHUA MP |  |  |  |  | BOILER HRSG TOH |  |  |  |  | BOILER HRSG TOH |  |  |  |  | BOILER HRSG GAS TURBIN |  |  |  |  | BOILER HRSG GAS TURBIN
BOILER PP #1 | [5 empty] | BOILER PP #2 |  |  |  |  | BOILER PP #3 |  |  |  |  | BOILER PP #4 |  |  |  |  | BOILER HP COAL |  |  |  |  | BOILER HP GAS |  |  |  |  | BOILER MP |  |  |  |  | BOILER TOH #3 |  |  |  |  | BOILER TOH #4 |  |  |  |  | BOILER HRSG GT #1 |  |  |  |  | BOILER HRSG GT #2
Date | Temperature Deaerator | Tekanan Operasi Boiler | Steam Flow Rate | Feed Water Flow Rate | Feed Water Temperature | Temperature Deaerator | Tekanan Operasi Boiler | Steam Flow Rate | Feed Water Flow Rate | Feed Water Temperature | Temperature Deaerator | Tekanan Operasi Boiler | Steam Flow Rate | Feed Water Flow Rate | Feed Water Temperature | Temperature Deaerator | Tekanan Operasi Boiler | Steam Flow Rate | Feed Water Flow Rate | Feed Water Temperature | Temperature Deaerator | Tekanan Operasi Boiler | Steam Flow Rate | Feed Water Flow Rate | Feed Water Temperature | Temperature Deaerator | Tekanan Operasi Boiler | Steam Flow Rate | Feed Water Flow Rate | Feed Water Temperature | Temperature Deaerator | Tekanan Operasi Boiler | Steam Flow Rate | Feed Water Flow Rate | Feed Water Temperature | Temperature Deaerator | Tekanan Operasi Boiler | Steam Flow Rate | Feed Water Flow Rate | Feed Water Temperature | Temperature Deaerator | Tekanan Operasi Boiler | Steam Flow Rate | Feed Water Flow Rate | Feed Water Temperature | Temperature Deaerator | Tekanan Operasi Boiler | Steam Flow Rate | Feed Water Flow Rate | Feed Water Temperature | Temperature Deaerator | Tekanan Operasi Boiler | Steam Flow Rate | Feed Water Flow Rate | Feed Water Temperature
| oC ( MIN 100 oC ) | kg/cm2 | m3/h | m3/h | oC | oC ( MIN 100 oC ) | kg/cm2 | m3/h | m3/h | oC | oC ( MIN 100 oC ) | kg/cm2 | m3/h | m3/h | oC | oC ( MIN 100 oC ) | kg/cm2 | m3/h | m3/h | oC | oC ( MIN 100 oC ) | kg/cm2 | m3/h | m3/h | oC | oC ( MIN 100 oC ) | kg/cm2 | m3/h | m3/h | oC | oC ( MIN 100 oC ) | kg/cm2 | m3/h | m3/h | oC | oC ( MIN 100 oC ) | kg/cm2 | m3/h | m3/h | oC | oC ( MIN 100 oC ) | kg/cm2 | m3/h | m3/h | oC | oC ( MIN 100 oC ) | kg/cm2 | m3/h | m3/h | oC | oC ( MIN 100 oC ) | kg/cm2 | m3/h | m3/h | oC
2020-05-01 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-02 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-03 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-04 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-05 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-06 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-07 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-08 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-09 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-10 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-11 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-12 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-13 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-14 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-15 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-16 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-17 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-18 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-19 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-20 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-21 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-22 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-23 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-24 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-25 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-26 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-27 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-28 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-29 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-30 | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | no data
2020-05-31 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
OVERALL VALUE
Date | BOILER PP | BOILER HP COAL | BOILER HP GAS | BOILER MP | BOILER TOH | BOILER HRSG
2020-05-01 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-02 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-03 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-04 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-05 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-06 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-07 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-08 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-09 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-10 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-11 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-12 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-13 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-14 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-15 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-16 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-17 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-18 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-19 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-20 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-21 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-22 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-23 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-24 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-25 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-26 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-27 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-28 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-29 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-30 | 100% | 100% | 100% | 100% | 100% | 100%
2020-05-31 | no data | no data | no data | no data | no data | no data
CONFORMANCE | 100% | 100% | 100% | 100% | 100% | 100%
FLOW STEAM
2020-05-01 | 100%
2020-05-02 | 100%
2020-05-03 | 100%
2020-05-04 | 100%
2020-05-05 | 100%
2020-05-06 | 100%
2020-05-07 | 100%
2020-05-08 | 100%
2020-05-09 | 100%
2020-05-10 | 100%
2020-05-11 | 100%
2020-05-12 | 100%
2020-05-13 | 100%
2020-05-14 | 100%
2020-05-15 | 100%
2020-05-16 | 100%
2020-05-17 | 100%
2020-05-18 | 100%
2020-05-19 | 100%
2020-05-20 | 100%
2020-05-21 | 100%
2020-05-22 | 100%
2020-05-23 | 100%
2020-05-24 | 100%
2020-05-25 | 100%
2020-05-26 | 100%
2020-05-27 | 100%
2020-05-28 | 100%
2020-05-29 | 100%
2020-05-30 | 100%
2020-05-31

## DEMIN WATER
| BUFFER DEMIN TANK |  |  |  |  | DEMIN TANK | [5 empty] | RODEM #1(DYNALON #1) | [11 empty] | RODEM #2 (DYNALON #2) | [11 empty] | RODEM #3 (DYNALON #4) | [11 empty] | RODEM #4 (NEW RO) | [10 empty] | MIXBED
[12 empty] | INLET SAND FILTER | OUTLET SAND FILTER | FEED RODEM #1 |  |  |  | PERMEATE RODEM #1 | [5 empty] | INLET SAND FILTER | OUTLET SAND FILTER | FEED RODEM #2 |  |  |  | PERMEATE RODEM #2 | [5 empty] | INLET SAND FILTER | OUTLET SAND FILTER | FEED RODEM #3 |  |  |  | PERMEATE RODEM #3 | [5 empty] | INLET SAND FILTER | OUTLET SAND FILTER | FEED RODEM #4 |  |  |  | PERMEATE RODEM #4 |  |  |  |  | MB #1A | [5 empty] | MB #1B | [5 empty] | MB #2A | [5 empty] | MB #2B | [5 empty] | MB #3A | [5 empty] | MB #3B | [5 empty] | MB #4
Parameter | pH | Conductivity | T. Hardness | Silica | Iron | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | Free Chlorine | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | Free Chlorine | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | Free Chlorine | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | Free Chlorine | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity
|  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU | (ppm Cl2) | NTU |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU | (ppm Cl2) | NTU |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU | (ppm Cl2) | NTU |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU | (ppm Cl2) | NTU |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU
| 5.5 - 7.0 | < 1.0 | 0.1; Max | 0.16 ; Max | 0.02 ; Max | 5.5 - 7.0 | < 25.0 | 0.1; Max | 0.16 ; Max | 0.05 ; Max | <1 | 0.20 - 0.50 | N/A | 6.0 - 6.5 | < 1000 | < 0.10 | < 0.50 | 5.0 - 7.0 | < 50 | 1.5 : Max | < 5 | < 0.10 |  | 0.20 - 0.50 | N/A | 6.0 - 6.5 | < 1000 | < 0.10 | < 0.50 | 5.0 - 7.0 | < 50 | 1.5 : Max | < 5 | < 0.10 |  | 0.20 - 0.50 | N/A | 6.0 - 6.5 | < 1000 | < 0.10 | < 0.50 | 5.0 - 7.0 | < 50 | 1.5 : Max | < 5 | < 0.10 |  | 0.20 - 0.50 | N/A | 6.0 - 6.5 | < 1000 | < 0.10 | < 0.50 | 5.0 - 7.0 | < 50 | 1.5 : Max | < 5 |  | 6.0 - 7.0 | < 1.0 | 0.10; Max | 0.16 ; Max | 0.05 ; Max | <1 | 6.0 - 7.0 | < 1.0 | 0.10; Max | 0.16 ; Max | 0.05 ; Max | <1 | 6.0 - 7.0 | < 1.0 | 0.10; Max | 0.16 ; Max | 0.05 ; Max | <1 | 6.0 - 7.0 | < 1.0 | 0.10; Max | 0.16 ; Max | 0.05 ; Max | <1 | 6.0 - 7.0 | < 1.0 | 0.10; Max | 0.16 ; Max | 0.05 ; Max | <1 | 6.0 - 7.0 | < 1.0 | 0.10; Max | 0.16 ; Max | 0.05 ; Max | <1 | 6.0 - 7.0 | < 1.0 | 0.10; Max | 0.16 ; Max | 0.05 ; Max | <1
Date
2026-09-01 | 6.44 | 0.89 |  |  |  | 6.19 | 1.21 | 0.047 | 0.025 | 0.01 | 0.26 | 0.37 | 0.25 | 6.5 | 830.9 | 0 | 0.25 | 5.75 | 18.92 | 0.06 | 0.319 | 0.01 | 0.39 | 0.39 | 0.45 | 6.47 | 832.8 | 0 | 0.3 | 5.66 | 22.59 | 0.6 | 0.324 | 0.01 | 0.24 | 0.48 | 0.4 | 6.39 | 845.7 | 0 | 0.29 | 5.59 | 29 | 0.25 | 0.586 | 0.02 | 0.23 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.23 | 0.74 | 0.041 | 0.01 | 0.01 | 0.4 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.18 | 0.93 | 0.021 | 0.011 | 0.02 | 0.33 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-02 | 6.76 | 0.91 |  |  |  | 6.5 | 0.9 | 0.07 | 0.012 | 0.01 | 0.3 | 0.35 | 0.29 | 6 | 898.3 | 0 | 0.19 | 5.41 | 22.19 | 0.08 | 0.183 | 0.01 | 0.23 | 0.33 | 0.19 | 6.3 | 782.1 | 0 | 0.25 | 5.14 | 48.5 | 0.12 | 0.164 | 0.02 | 0.22 | 0.46 | 0.28 | 6.1 | 882.8 | 0 | 0.25 | 5.41 | 30.11 | 0.15 | 0.213 | 0.01 | 0.35 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.58 | 0.62 | 0.017 | 0.012 | 0.01 | 0.25 | 6.36 | 0.77 | 0.019 | 0.012 | 0.02 | 0.23 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-03 | 6.19 | 0.92 |  |  |  | 6.57 | 1.55 | 0.065 | 0.125 | 0.02 | 0.46 | 0.31 | 0.22 | 6.38 | 791.6 | 0 | 0.22 | 5.78 | 18.77 | 0.09 | 0.286 | 0.01 | 0.53 | 0.33 | 0.51 | 6.24 | 797.5 | 0 | 0.26 | 5.64 | 25.91 | 0.11 | 0.259 | 0.01 | 0.27 | 0.27 | 0.19 | 6.36 | 665.8 | 0 | 0.17 | 5.68 | 22.8 | 0.08 | 0.483 | 0.01 | 0.19 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.11 | 0.66 | 0.04 | 0.023 | 0.02 | 0.67 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.23 | 0.98 | 0.046 | 0.016 | 0.01 | 0.46 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-04 | 6.3 | 0.95 |  |  |  | 6.4 | 1.35 | 0.062 | 0.03 | 0.01 | 0.46 | 0.41 | 0.45 | 6.5 | 782.1 | 0 | 0.35 | 5.61 | 16.71 | 0.11 | 0.331 | 0.04 | 0.21 | 0.42 | 0.32 | 6.27 | 774.7 | 0 | 0.19 | 5.39 | 28.88 | 0.18 | 0.291 | 0.02 | 0.15 | 0.29 | 0.38 | 6.43 | 720 | 0 | 0.24 | 5.44 | 24.39 | 0.2 | 0.465 | 0.01 | 0.2 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.63 | 0.77 | 0.072 | 0.013 | 0.01 | 0.34 | 6.44 | 0.94 | 0.035 | 0.013 | 0.01 | 0.29 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-05 | 6.54 | 0.74 |  |  |  | 6.7 | 1.4 | 0.032 | 0.022 | 0.02 | 0.34 | 0.4 | 0.47 | 6.48 | 714.1 | 0 | 0.24 | 5.82 | 14.5 | 0.1 | 0.352 | 0.01 | 0.22 | 0.32 | 0.22 | 6.47 | 742.8 | 0 | 0.17 | 5.61 | 21.5 | 0.09 | 0.299 | 0.02 | 0.15 | 0.48 | 0.45 | 6.42 | 750.2 | 0 | 0.36 | 5.8 | 23.77 | 0.07 | 0.524 | 0.02 | 0.27 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.4 | 0.98 | 0.019 | 0.01 | 0.01 | 0.18 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.6 | 0.9 | 0.027 | 0.013 | 0.02 | 0.31 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-06 | 6.49 | 0.95 |  |  |  | 6.72 | 11.43 | 0.092 | 0.136 | 0.03 | 0.42
2026-09-07 | 6.42 | 0.98 |  |  |  | 6.75 | 1.96 | 0.022 | 0.025 | 0.01 | 0.44 | 0.37 | 0.32 | 6.35 | 688.4 | 0 | 0.23 | 5.76 | 13.54 | 0.11 | 0.365 | 0.02 | 0.31 | 0.45 | 0.3 | 6.33 | 700 | 0 | 0.21 | 5.58 | 18.26 | 0.09 | 0.269 | 0.02 | 0.27 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.41 | 0.84 | 0.009 | 0.04 | 0.01 | 0.19 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.58 | 0.93 | 0.011 | 0.014 | 0.01 | 0.2 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-08 | 6.4 | 0.91 |  |  |  | 6.58 | 1.77 | 0.06 | 0.03 | 0.01 | 0.39 | 0.3 | 0.51 | 6.38 | 654.4 | 0 | 0.27 | 5.69 | 13.2 | 0.08 | 0.263 | 0.02 | 0.27 | 0.5 | 0.66 | 6.28 | 661.8 | 0 | 0.38 | 5.61 | 15.41 | 0.06 | 0.256 | 0.01 | 0.22 | 0.45 | 0.43 | 6.4 | 649.4 | 0 | 0.25 | 5.59 | 20.86 | 0.17 | 0.536 | 0.02 | 0.24 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.59 | 0.71 | 0.009 | 0.017 | 0.02 | 0.29 | 6.29 | 0.89 | 0.009 | 0.012 | 0.02 | 0.26 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-09 | 6.36 | 0.97 |  |  |  | 6.51 | 1.47 | 0.072 | 0.149 | 0.01 | 0.41 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.35 | 0.76 | 0.018 | 0.137 | 0.01 | 0.2 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.43 | 0.94 | 0.016 | 0.021 | 0.01 | 0.36 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-10 | 6.31 | 0.9 |  |  |  | 6.54 | 1.25 | 0.013 | 0.031 | 0.01 | 0.37 | 0.27 | 0.48 | 6.32 | 613.5 | 0 | 0.21 | 5.64 | 13.09 | 0.03 | 0.325 | 0.02 | 0.23 | 0.42 | 0.57 | 6.29 | 628.2 | 0 | 0.33 | 5.6 | 21.26 | 0.05 | 0.299 | 0.02 | 0.26 | 0.5 | 0.37 | 6.38 | 600.1 | 0.01 | 0.27 | 5.5 | 21.15 | 0.06 | 0.52 | 0.02 | 0.2 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.43 | 0.75 | 0.006 | 0.016 | 0.01 | 0.28 | 6.78 | 0.18 | 0.011 | 0.012 | 0.01 | 0.22 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-11 | 6.29 | 0.86 |  |  |  | 6.38 | 1.55 | 0.039 | 0.03 | 0.01 | 0.36 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 0.43 | 0.99 | 6.31 | 673.3 | 0 | 0.27 | 5.54 | 22.07 | 0.07 | 0.342 | 0.02 | 0.33 | 0.37 | 0.41 | 6.3 | 659 | 0 | 0.23 | 5.68 | 24.43 | 0.08 | 0.512 | 0.02 | 0.36 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.4 | 0.71 | 0.012 | 0.013 | 0.01 | 0.35 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.4 | 0.88 | 0.03 | 0.028 | 0.01 | 0.38 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-12 | 6.35 | 0.93 |  |  |  | 6.4 | 1.24 | 0.074 | 0.004 | 0.02 | 0.27 | 0.25 | 0.59 | 6.28 | 734.8 | 0 | 0.23 | 5.79 | 24.07 | 0.1 | 0.15 | 0.01 | 0.29 | 0.5 | 0.62 | 6.18 | 759.5 | 0.01 | 0.22 | 5.42 | 26.56 | 0.09 | 0.141 | 0.01 | 0.27 | 0.5 | 0.86 | 6.14 | 734.2 | 0.01 | 0.24 | 5.52 | 27.33 | 0.07 | 0.154 | 0.01 | 0.26 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.5 | 0.9 | 0.077 | 0.005 | 0.02 | 0.29 | 6.54 | 0.89 | 0.078 | 0.004 | 0.01 | 0.31 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-13 | 6.42 | 0.62 |  |  |  | 6.55 | 0.81 | 0.047 | 0.128 | 0.01 | 0.23
2026-09-14 | 6.27 | 0.76 |  |  |  | 6.33 | 0.78 | 0.084 | 0.01 | 0.04 | 0.27 | 0.35 | 0.38 | 6.01 | 753.1 | 0 | 0.3 | 5.27 | 24.02 | 0.07 | 0.09 | 0.02 | 0.2 | 0.48 | 0.45 | 6.25 | 754.1 | 0.01 | 0.34 | 5.35 | 21.45 | 0.07 | 0.119 | 0.01 | 0.27 | 0.4 | 0.55 | 6.28 | 653.4 | 0 | 0.24 | 5.43 | 23.05 | 0.11 | 0.495 | 0.01 | 0.24 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.42 | 0.96 | 0.042 | 0.01 | 0.05 | 0.27 | 6.3 | 0.92 | 0.033 | 0.01 | 0.05 | 0.45 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-15 | 6.51 | 0.97 |  |  |  | 6.6 | 1.31 | 0.067 | 0.033 | 0.03 | 0.5 | 0.43 | 0.33 | 6.49 | 819.4 | 0 | 0.4 | 5.38 | 18.83 | 0.14 | 0.143 | 0.02 | 0.26 | 0.28 | 0.36 | 6.49 | 828.7 | 0 | 0.38 | 5.4 | 24.58 | 0.12 | 0.159 | 0.01 | 0.29 | 0.23 | 0.33 | 6.45 | 829.2 | 0 | 0.43 | 5.58 | 29.07 | 0.15 | 0.177 | 0.02 | 0.43 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.61 | 0.98 | 0.041 | 0.021 | 0.03 | 0.35 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.39 | 0.95 | 0.031 | 0.046 | 0.01 | 0.28 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-16 | 6.24 | 0.99 |  |  |  | 6.27 | 0.88 | 0.048 | 0.071 | 0.03 | 0.24 | 0.35 | 0.25 | 6.38 | 855.9 | 0 | 0.47 | 5.3 | 19.21 | 0.08 | 0.431 | 0.02 | 0.32 | 0.31 | 0.28 | 6.49 | 853.3 | 0 | 0.21 | 5.33 | 22.82 | 0.21 | 0.347 | 0.02 | 0.49 | 0.5 | 0.4 | 6.3 | 843.2 | 0 | 0.5 | 5.4 | 30.89 | 0.13 | 0.282 | 0.02 | 0.26 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.8 | 0.9 | 0.064 | 0.014 | 0.01 | 0.21 | 6.54 | 0.97 | 0.035 | 0.022 | 0.02 | 0.22 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-17 | 6.44 | 0.86 |  |  |  | 6.38 | 1.29 | 0.03 | 0.054 | 0.04 | 0.46 | 0.48 | 0.3 | 6.42 | 929.8 | 0 | 0.28 | 5.52 | 22.64 | 0.08 | 0.228 | 0.01 | 0.36 | 0.2 | 0.48 | 6.43 | 929.8 | 0 | 0.27 | 5.56 | 54.29 | 0.28 | 0.4 | 0.02 | 0.29 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.57 | 0.41 | 0.075 | 0.047 | 0.03 | 0.38 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.41 | 0.59 | 0.049 | 0.038 | 0.04 | 0.25 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-18 | 6.55 | 0.94 |  |  |  | 6.4 | 1 | 0.092 | 0.05 | 0.03 | 0.28 | 0.46 | 0.53 | 6.27 | 838.6 | 0 | 0.5 | 5.14 | 45.41 | 0.1 | 0.23 | 0.02 | 0.58 | 0.2 | 0.49 | 6.03 | 839.5 | 0 | 0.5 | 5.36 | 39.15 | 0.13 | 0.106 | 0.01 | 0.35 | 0.2 | 0.79 | 6.31 | 928.1 | 0 | 0.5 | 5.6 | 33.92 | 0.108 | 0.14 | 0.01 | 0.26 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.5 | 0.89 | 0.058 | 0.03 | 0.04 | 0.29 | 6.39 | 0.98 | 0.024 | 0.048 | 0.01 | 0.48 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-19 | 6.57 | 0.9 |  |  |  | 6.31 | 0.96 | 0.038 | 0.123 | 0.01 | 0.24 | 0.48 | 0.18 | 6.02 | 906.8 | 0 | 0.23 | 5.48 | 21.67 | 0.13 | 0.249 | 0.01 | 0.25 | 0.24 | 0.49 | 6.03 | 992 | 0 | 0.5 | 5.36 | 39.15 | 0.15 | 0.106 | 0.01 | 0.35 | 0.27 | 0.25 | 6.14 | 854.7 | 0 | 0.24 | 5.57 | 27.03 | 0.11 | 0.421 | 0.01 | 0.35 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.21 | 0.69 | 0.012 | 0.022 | 0.01 | 0.15 | stop | stop | stop | stop | stop | stop | 6.08 | 0.8 | 0.015 | 0.014 | 0.02 | 0.22 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-20 | 6.97 | 0.93 |  |  |  | 6.41 | 0.99 | 0.058 | 0.081 | 0.01 | 0.63
2026-09-21 | 6.3 | 0.98 |  |  |  | 6.52 | 1 | 0.032 | 0.042 | 0.02 | 0.42 | 0.5 | 0.29 | 6.05 | 769.8 | 0 | 0.26 | 5.82 | 19.84 | 0.06 | 0.247 | 0.03 | 0.26 | 0.48 | 0.63 | 6.25 | 805.3 | 0 | 0.48 | 5.66 | 27.42 | 0.11 | 0.335 | 0.02 | 0.33 | 0.5 | 0.39 | 6.29 | 847.5 | 0 | 0.6 | 5.77 | 28.03 | 0.02 | 0.241 | 0.02 | 0.29 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.34 | 0.81 | 0.067 | 0.049 | 0.01 | 0.25 | 6.11 | 0.98 | 0.068 | 0.027 | 0.01 | 0.29 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-22 | 6.61 | 0.75 |  |  |  | 6.4 | 0.95 | 0.038 | 0.092 | 0.02 | 0.36 | 0.42 | 0.23 | 6.01 | 747.6 | 0 | 0.26 | 5.96 | 19.24 | 0.05 | 0.278 | 0.02 | 0.17 | 0.38 | 0.25 | 6.13 | 771.1 | 0 | 0.2 | 5.68 | 24.73 | 0.02 | 0.3 | 0.02 | 0.24 | 0.4 | 0.29 | 6.25 | 777.1 | 0 | 0.23 | 5.73 | 24.44 | 0.02 | 0.336 | 0.03 | 0.23 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.21 | 0.21 | 0.037 | 0.02 | 0.02 | 0.17 | stop | stop | stop | stop | stop | stop | 6.22 | 0.93 | 0.077 | 0.017 | 0.02 | 0.2 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-23 | 6.7 | 0.93 |  |  |  | 6.3 | 0.97 | 0.049 | 0.066 | 0.01 | 0.36 | 0.2 | 0.83 | 6.08 | 1048 | 0 | 0.4 | 5.63 | 25.33 | 0.13 | 0.348 | 0.02 | 0.34 | 0.5 | 0.51 | 6.16 | 1070 | 0 | 0.25 | 5.7 | 31.72 | 0.15 | 0.401 | 0.02 | 0.39 | 0.4 | 0.29 | 6.25 | 777.1 | 0 | 0.23 | 5.73 | 24.44 | 0.02 | 0.36 | 0.03 | 0.23 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.38 | 0.87 | 0.019 | 0.012 | 0.01 | 0.28 | stop | stop | stop | stop | stop | stop | 6.26 | 0.9 | 0.018 | 0.011 | 0.01 | 0.26 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-24 | 6.92 | 0.98 |  |  |  | 6.49 | 0.85 | 0.038 | 0.067 | 0.02 | 0.66 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 0.23 | 0.72 | 6.03 | 784.3 | 0 | 0.5 | 5.94 | 22.21 | 0.03 | 0.496 | 0.02 | 0.47 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.45 | 0.78 | 0.035 | 0.067 | 0.01 | 0.22 | stop | stop | stop | stop | stop | stop | 6.29 | 0.79 | 0.051 | 0.043 | 0.02 | 0.19 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-25 | 6.64 | 0.93 |  |  |  | 6.45 | 0.94 | 0.021 | 0.024 | 0.02 | 0.76 | 0.28 | 1.2 | 6.12 | 731.4 | 0 | 0.34 | 5.82 | 15.16 | 0.06 | 0.185 | 0.02 | 0.43 | 0.27 | 0.35 | 6.39 | 744.3 | 0 | 0.36 | 5.75 | 20.44 | 0.24 | 0.233 | 0.01 | 0.47 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.45 | 0.61 | 0.021 | 0.009 | 0.01 | 0.4 | stop | stop | stop | stop | stop | stop | 6.32 | 0.74 | 0.02 | 0.006 | 0.01 | 0.42 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-26 | 6.69 | 0.91 |  |  |  | 6.57 | 0.87 | 0.016 | 0.068 | 0.01 | 0.28 | 0.4 | 0.24 | 6.35 | 578.6 | 0 | 0.21 | 5.95 | 12.78 | 0.1 | 0.272 | 0.01 | 0.28 | 0.49 | 0.17 | 6.42 | 601.7 | 0 | 0.27 | 5.99 | 15.9 | 0.13 | 0.337 | 0.01 | 0.32 | 0.5 | 0.24 | 6.5 | 630 | 0.01 | 0.4 | 5.76 | 19.14 | 0.28 | 0.371 | 0.01 | 0.23 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.36 | 0.98 | 0.033 | 0.018 | 0.01 | 0.38 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-27 | 6.65 | 0.93 |  |  |  | 6.48 | 0.67 | 0.031 | 0.037 | 0.02 | 0.22
2026-09-28 | 6.36 | 0.63 |  |  |  | 6.16 | 0.78 | 0.031 | 0.102 | 0.02 | 0.33 | 0.42 | 0.23 | 6.46 | 807.5 | 0 | 0.23 | 5.62 | 15.1 | 0.1 | 0.315 | 0.01 | 0.22 | 0.46 | 0.42 | 6.5 | 806.2 | 0.01 | 0.17 | 5.56 | 18.86 | 0.23 | 0.388 | 0.02 | 0.29 | 0.46 | 0.36 | 6.46 | 852.9 | 0.01 | 0.27 | 5.49 | 26.13 | 0.21 | 0.439 | 0.01 | 0.22 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.37 | 0.56 | 0.018 | 0.003 | 0.01 | 0.26 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.36 | 0.9 | 0.045 | 0.027 | 0.02 | 0.2 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-29 | 6.8 | 0.83 |  |  |  | 6.55 | 0.83 | 0.036 | 0.033 | 0.01 | 0.5 | 0.31 | 0.34 | 6.5 | 800.8 | 0 | 0.31 | 5.65 | 15.38 | 0.07 | 0.349 | 0.02 | 0.26 | 0.46 | 0.34 | 6.47 | 802.6 | 0.01 | 0.24 | 5.67 | 20.64 | 0.21 | 0.499 | 0.02 | 0.24 | 0.5 | 0.39 | 6.5 | 830.4 | 0.01 | 0.29 | 5.69 | 25.02 | 0.1 | 0.545 | 0.01 | 0.23 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.5 | 0.58 | 0.019 | 0.021 | 0.02 | 0.47 | 6.18 | 0.98 | 0.042 | 0.007 | 0.01 | 0.46 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-30 | 6.87 | 0.94 |  | 0.034 |  | 6.66 | 1.21 | 0.083 | 0.352 | 0.02 | 0.42 | 0.2 | 0.38 | 6.5 | 719 | 0 | 0.34 | 5.64 | 13.41 | 0.07 | 0.43 | 0.01 | 0.18 | 0.23 | 0.18 | 6.5 | 721.3 | 0 | 0.32 | 5.86 | 18.54 | 0.25 | 0.632 | 0.01 | 0.23 | 0.48 | 0.29 | 6.47 | 737.8 | 0 | 0.28 | 5.96 | 22.06 | 0.12 | 0.694 | 0.01 | 0.27 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.45 | 0.7 | 0.014 | 0.041 | 0.01 | 0.36 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.48 | 0.89 | 0.016 | 0.02 | 0.01 | 0.36 | [12 empty] | stop | stop | stop | stop | stop | stop
2026-10-01
| BUFFER DEMIN TANK |  |  |  |  | DEMIN TANK | [5 empty] | RODEM #1(DYNALON #1) | [11 empty] | RODEM #2 (DYNALON #2) | [11 empty] | RODEM #3 (DYNALON #4) | [11 empty] | RODEM #4 (NEW RO) | [10 empty] | MIXBED
[12 empty] | INLET SAND FILTER | OUTLET SAND FILTER | FEED RODEM #1 |  |  |  | PERMEATE RODEM #1 | [5 empty] | INLET SAND FILTER | OUTLET SAND FILTER | FEED RODEM #2 |  |  |  | PERMEATE RODEM #2 | [5 empty] | INLET SAND FILTER | OUTLET SAND FILTER | FEED RODEM #3 |  |  |  | PERMEATE RODEM #3 | [5 empty] | INLET SAND FILTER | OUTLET SAND FILTER | FEED RODEM #4 |  |  |  | PERMEATE RODEM #4 |  |  |  |  | MB #1A | [5 empty] | MB #1B | [5 empty] | MB #2A | [5 empty] | MB #2B | [5 empty] | MB #3A | [5 empty] | MB #3B | [5 empty] | MB #4
Parameter | pH | Conductivity | T. Hardness | Silica | Iron | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | Free Chlorine | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | Free Chlorine | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | Free Chlorine | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | Free Chlorine | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity
|  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU | (ppm Cl2) | NTU |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU | (ppm Cl2) | NTU |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU | (ppm Cl2) | NTU |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU | (ppm Cl2) | NTU |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU
| 5.5 - 7.0 | < 1.0 | 0.1; Max | 0.16 ; Max | 0.02 ; Max | 5.5 - 7.0 | < 25.0 | 0.1; Max | 0.16 ; Max | 0.05 ; Max | <1 | 0.20 - 0.50 | N/A | 6.0 - 6.5 | < 1000 | < 0.10 | < 0.50 | 5.0 - 7.0 | < 50 | 1.5 : Max | < 5 | < 0.10 |  | 0.20 - 0.50 | N/A | 6.0 - 6.5 | < 1000 | < 0.10 | < 0.50 | 5.0 - 7.0 | < 50 | 1.5 : Max | < 5 | < 0.10 |  | 0.20 - 0.50 | N/A | 6.0 - 6.5 | < 1000 | < 0.10 | < 0.50 | 5.0 - 7.0 | < 50 | 1.5 : Max | < 5 | < 0.10 |  | 0.20 - 0.50 | N/A | 6.0 - 6.5 | < 1000 | < 0.10 | < 0.50 | 5.0 - 7.0 | < 50 | 1.5 : Max | < 5 |  | 6.0 - 7.0 | < 1.0 | 0.10; Max | 0.16 ; Max | 0.05 ; Max | <1 | 6.0 - 7.0 | < 1.0 | 0.10; Max | 0.16 ; Max | 0.02 ; Max | <1 | 6.0 - 7.0 | < 1.0 | 0.10; Max | 0.16 ; Max | 0.05 ; Max | <1 | 6.0 - 7.0 | < 1.0 | 0.10; Max | 0.16 ; Max | 0.05 ; Max | <1 | 6.0 - 7.0 | < 1.0 | 0.10; Max | 0.16 ; Max | 0.05 ; Max | <1 | 6.0 - 7.0 | < 1.0 | 0.10; Max | 0.16 ; Max | 0.05 ; Max | <1 | 6.0 - 7.0 | < 1.0 | 0.10; Max | 0.16 ; Max | 0.05 ; Max | <1
2026-09-01 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-02 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-03 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-04 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-05 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-06 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data |  | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-07 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-08 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-09 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-10 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-11 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-12 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-13 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data |  | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-14 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-15 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-16 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-17 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-18 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-19 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-20 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data |  | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-21 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-22 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-23 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-24 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-25 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-26 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-27 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data |  | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-28 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-29 | 100% | 100% | no data | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-30 | 100% | 100% | no data | 100% | no data | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | stop | stop |  | stop |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | stop | stop | stop | stop | stop | stop
2026-10-01 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data |  | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
Conformance | 100% | 100% |  | 100% |  | 100% | 100% | 100% | 96.67% | 100% | 100% | 100% | 100% | 100% | 95.65% | 100% | 100% | 100% | 100% |  | 100% |  |  | 100% | 100% | 100% | 95.83% | 100% | 100% | 100% | 95.83% |  | 100% |  |  | 100% | 100% | no data | 100% | 100% | 95.45% | 100% | 100% |  | 100% | [13 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
OVERALL VALUE
Date | DEMIN TANK | DYNALON #1 |  |  |  | MIXBED | DYNALON #2 | DYNALON #4 | NEW RO | BUFFFER DEMIN
2026-09-01 | 100% | 100% |  |  |  | 100% | 100% | 100% | stop | 100%
2026-09-02 | 100% | 100% |  |  |  | stop | 100% | 100% | stop | 100%
2026-09-03 | 100% | 100% |  |  |  | 100% | 100% | 100% | stop | 100%
2026-09-04 | 100% | 100% |  |  |  | stop | 100% | 100% | stop | 100%
2026-09-05 | 100% | 100% |  |  |  | 100% | 100% | 100% | stop | 100%
2026-09-06 | 100% | no data |  |  |  | no data | no data | no data | no data | 100%
2026-09-07 | 100% | 100% |  |  |  | 100% | 100% | stop | stop | 100%
2026-09-08 | 100% | 100% |  |  |  | stop | 100% | 100% | stop | 100%
2026-09-09 | 100% | stop |  |  |  | 100% | stop | stop | stop | 100%
2026-09-10 | 100% | 100% |  |  |  | stop | 100% | 100% | stop | 100%
2026-09-11 | 100% | stop |  |  |  | 100% | 100% | 100% | stop | 100%
2026-09-12 | 100% | 100% |  |  |  | stop | 100% | 100% | stop | 100%
2026-09-13 | 100% | no data |  |  |  | no data | no data | no data | no data | 100%
2026-09-14 | 100% | 100% |  |  |  | stop | 100% | 100% | stop | 100%
2026-09-15 | 100% | 100% |  |  |  | 100% | 100% | 100% | stop | 100%
2026-09-16 | 100% | 100% |  |  |  | stop | 100% | 100% | stop | 100%
2026-09-17 | 100% | 100% |  |  |  | 100% | 90.91% | stop | stop | 100%
2026-09-18 | 100% | 100% |  |  |  | stop | 100% | 100% | stop | 100%
2026-09-19 | 100% | 100% |  |  |  | 100% | 100% | 100% | stop | 100%
2026-09-20 | 100% | no data |  |  |  | no data | no data | no data | no data | 100%
2026-09-21 | 100% | 100% |  |  |  | stop | 100% | 90.91% | stop | 100%
2026-09-22 | 100% | 100% |  |  |  | stop | 100% | 100% | stop | 100%
2026-09-23 | 100% | 90% |  |  |  | 100% | 90.91% | 100% | stop | 100%
2026-09-24 | 100% | stop |  |  |  | stop | stop | 100% | stop | 100%
2026-09-25 | 100% | 100% |  |  |  | 100% | 100% | stop | stop | 100%
2026-09-26 | 100% | 100% |  |  |  | stop | 100% | 100% | stop | 100%
2026-09-27 | 100% | no data |  |  |  | no data | no data | no data | no data | 100%
2026-09-28 | 100% | 100% |  |  |  | 100% | 100% | 100% | stop | 100%
2026-09-29 | 100% | 100% |  |  |  | stop | 100% | 100% | stop | 100%
2026-09-30 | 83.33% | 100% |  |  |  | 100% | 100% | 100% | stop | 100%
2026-10-01 | no data | no data |  |  |  | no data | no data | no data | no data | no data
Conformance | 99.44% | 99.57% |  |  |  | 100% | 99.24% | 99.59% |  | 100%
RO & MMF
2026-09-01 | 100%
2026-09-02 | 100%
2026-09-03 | 100%
2026-09-04 | 100%
2026-09-05 | 100%
2026-09-06 | 100%
2026-09-07 | 100%
2026-09-08 | 100%
2026-09-09 | 100%
2026-09-10 | 100%
2026-09-11 | 100%
2026-09-12 | 100%
2026-09-13 | 100%
2026-09-14 | 100%
2026-09-15 | 100%
2026-09-16 | 100%
2026-09-17 | 97.73%
2026-09-18 | 100%
2026-09-19 | 100%
2026-09-20 | 100%
2026-09-21 | 97.73%
2026-09-22 | 100%
2026-09-23 | 96.18%
2026-09-24 | 100%
2026-09-25 | 100%
2026-09-26 | 100%
2026-09-27 | 100%
2026-09-28 | 100%
2026-09-29 | 100%
2026-09-30 | 96.67%
2026-10-01

## WTP #3
| RO TANK 600 MT | [6 empty] | DEMIN TANK BWRO | [5 empty] | RODEM #4A & RODEM #4B | [21 empty] | MIXBED | [11 empty] | RODOM #5 (RO 80)
[14 empty] | INLET SAND FILTER | OUTLET SAND FILTER | FEED RODEM #4A |  |  |  | FEED RODEM #4B |  |  |  | PERMEATE RO #4A | [5 empty] | PERMEATE RO #4B | [5 empty] | MB #5A | [5 empty] | MB #5B | [5 empty] | REJECT WATER TANK - RO #150 | [6 empty] | FEED RO After N- 7408 |  |  | PERMEATE RO RODOM #4
Parameter | pH | Conductivity | T. Hardness | Silica | Iron | Chloride | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | Free Chlorine | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Chloride | Turbidity | pH | Conductivity | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride
|  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppmCl-) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU | (ppm Cl2) | NTU |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppmCl-) | NTU |  | (µS/cm) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-)
| 5.0 - 7.0 | < 50 | 1.5; Max | < 5 | < 0.10 | < 30 | <1 | 5.5 - 7.0 | < 1.0 | 0.1; Max | 0.16 ; Max | 0.05 ; Max | <1 | 0.20 - 0.50 | N/A | 6.0 - 6.5 | < 1000 | < 0.10 | < 0.50 | 6.0 - 6.5 | < 1000 | < 0.10 | < 0.50 | 5.0 - 7.0 | < 50 | 1.5 : Max | < 5 | < 0.10 |  | 5.0 - 7.0 | < 50 | 1.5 : Max | < 5 | < 0.10 |  | 6.0 - 7.0 | 1.0 ; Max | 0.10; Max | 0.16 ; Max | 0.05 ; Max | <1 | 6.0 - 7.0 | 1.0 ; Max | 0.10; Max | 0.16 ; Max | 0.05 ; Max | <1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 6.0-6.5 | N/A | N/A | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A
Date
2026-09-01 | 6.01 | 18.54 | 0.29 | 0.267 | 0.02 | 4.856 | 0.35 | 6.51 | 0.5 | 0.016 | 0.027 | 0.02 | 0.35 | 0.26 | 0.37 | stop | stop | stop | stop | 6.4 | 737.9 | 0 | 0.36 | stop | stop | stop | stop | stop | stop | 5.84 | 15.6 | 0.48 | 0.257 | 0.02 | 0.59 | stop | stop | stop | stop | stop | stop | 6.74 | 0.43 | 0.093 | 0.006 | 0.02 | 0.28 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-02 | 5.73 | 13.93 | 0.26 | 0.345 | 0.02 | 4.856 | 0.22 | 6.47 | 0.67 | 0.047 | 0.012 | 0.01 | 0.38 | 0.46 | 0.24 | stop | stop | stop | stop | 6.05 | 651.1 | 0 | 0.19 | stop | stop | stop | stop | stop | stop | 5.45 | 13.24 | 0.13 | 0.196 | 0.02 | 0.23 | stop | stop | stop | stop | stop | stop | 6.73 | 0.45 | 0.042 | 0.012 | 0.01 | 0.3 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-03 | 5.49 | 13.45 | 0.21 | 0.143 | 0.02 | 4.856 | 0.33 | 6.54 | 0.95 | 0.014 | 0.01 | 0.02 | 0.3 | 0.41 | 0.18 | stop | stop | stop | stop | 6.16 | 666.7 | 0 | 0.25 | stop | stop | stop | stop | stop | stop | 5.58 | 12.1 | 0.14 | 0.139 | 0.01 | 0.22 | 6.66 | 0.7 | 0.054 | 0.011 | 0.02 | 0.32 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-04 | 5.79 | 14.98 | 0.24 | 0.35 | 0.01 | 4.856 | 0.56 | 6.6 | 0.64 | 0.025 | 0.08 | 0.02 | 0.22 | 0.35 | 0.28 | stop | stop | stop | stop | 6.4 | 573.3 | 0 | 0.25 | stop | stop | stop | stop | stop | stop | 5.64 | 14.41 | 0.21 | 0.275 | 0.01 | 0.25 | 6.52 | 0.43 | 0.017 | 0.08 | 0.01 | 0.27 | stop | stop | stop | stop | stop | stop | 7.37 | 3170 | 212 | 134 | 0.11 | 743.42 | 0.34 | 7.07 | 2200 | 0.3 | 5.96 | 158.4 | 10 | 8 | 42.28
2026-09-05 | 5.45 | 15.8 | 0.19 | 0.227 | 0.02 | 3.648 | 0.29 | 6.53 | 0.84 | 0.008 | 0.015 | 0.02 | 0.29 | 0.35 | 0.34 | 6.18 | 643.3 | 0 | 0.33 | stop | stop | stop | stop | 5.82 | 15.64 | 0.24 | 0.315 | 0.03 | 0.33 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.67 | 0.46 | 0.049 | 0.01 | 0.02 | 0.25 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-06 | 5.4 | 13.73 | 0.23 | 0.241 | 0.02 | 3.642 | 0.36 | 6.57 | 0.47 | 0.036 | 0.024 | 0.01 | 0.18
2026-09-07 | 5.78 | 17.86 | 0.34 | 0.374 | 0.02 | 6.17 | 0.46 | 6.53 | 0.74 | 0.068 | 0.013 | 0.01 | 0.22 | 0.28 | 0.3 | 6.15 | 509.6 | 0 | 0.27 | stop | stop | stop | stop | 5.71 | 14.09 | 0.34 | 0.355 | 0.01 | 0.48 | stop | stop | stop | stop | stop | stop | 6.58 | 0.49 | 0.04 | 0.004 | 0.01 | 0.29 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-08 | 5.67 | 14.97 | 0.17 | 0.334 | 0.02 | 3.642 | 0.3 | 6.64 | 0.91 | 0.015 | 0.01 | 0.01 | 0.25 | 0.21 | 0.26 | 6.3 | 698 | 0 | 0.34 | stop | stop | stop | stop | 5.45 | 14.88 | 0.17 | 0.346 | 0.02 | 0.27 | stop | stop | stop | stop | stop | stop | 6.6 | 0.68 | 0.026 | 0.043 | 0.01 | 0.34 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-09 | 5.68 | 14.99 | 0.28 | 0.452 | 0.02 | 6.07 | 0.16 | 6.31 | 0.47 | 0.029 | 0.021 | 0.01 | 0.2 | 0.23 | 0.18 | 6.22 | 683.9 | 0 | 0.25 | stop | stop | stop | stop | 5.36 | 15.42 | 0.23 | 0.529 | 0.01 | 0.17 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.18 | 0.29 | 0.03 | 0.02 | 0.01 | 0.19 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-10 | 5.51 | 15.11 | 0.22 | 0.395 | 0.01 | 4.856 | 0.22 | 6.27 | 0.38 | 0.021 | 0.061 | 0.01 | 0.24 | 0.2 | 0.18 | stop | stop | stop | stop | 6.33 | 680.9 | 0 | 0.28 | stop | stop | stop | stop | stop | stop | 5.52 | 15.46 | 0.18 | 0.514 | 0.02 | 0.19 | stop | stop | stop | stop | stop | stop | 6.3 | 0.52 | 0.011 | 0.058 | 0.01 | 0.21 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-11 | 5.57 | 14.66 | 0.2 | 0.294 | 0.01 | 4.856 | 0.2 | 6.39 | 0.71 | 0.078 | 0.023 | 0.01 | 0.21 | 0.5 | 0.19 | stop | stop | stop | stop | 6.31 | 689.3 | 0 | 0.25 | stop | stop | stop | stop | stop | stop | 5.5 | 15.41 | 0.21 | 0.335 | 0.01 | 0.23 | 6.42 | 0.57 | 0.028 | 0.005 | 0.01 | 0.22 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-12 | 5.74 | 11.86 | 0.21 | 0.133 | 0.01 | 3.642 | 0.25 | 6.28 | 0.64 | 0.034 | 0.004 | 0.02 | 0.24 | 0.5 | 0.48 | stop | stop | stop | stop | 6.21 | 626.4 | 0.01 | 0.23 | stop | stop | stop | stop | stop | stop | 5.28 | 11.27 | 0.38 | 0.119 | 0.01 | 0.2 | 6.38 | 0.67 | 0.032 | 0.002 | 0.01 | 0.25 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-13 | 5.39 | 11.07 | 0.16 | 0.208 | 0.01 | 3.642 | 0.22 | 6.54 | 0.44 | 0.057 | 0.018 | 0.04 | 0.32
2026-09-14 | 5.65 | 11.81 | 0.25 | 0.327 | 0.02 | 3.642 | 0.42 | 6.4 | 0.29 | 0.022 | 0.01 | 0.02 | 0.27 | 0.2 | 0.43 | stop | stop | stop | stop | 6.2 | 697.1 | 0.01 | 0.24 | stop | stop | stop | stop | stop | stop | 5.14 | 11.88 | 0.17 | 0.269 | 0.03 | 0.3 | stop | stop | stop | stop | stop | stop | 6.38 | 0.29 | 0.01 | 0.022 | 0.05 | 0.22 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-15 | 5.7 | 14.02 | 0.19 | 0.149 | 0.05 | 3.642 | 0.5 | 6.31 | 0.38 | 0.025 | 0.023 | 0.01 | 0.27 | 0.36 | 0.34 | stop | stop | stop | stop | 6.38 | 726.5 | 0 | 0.41 | stop | stop | stop | stop | stop | stop | 5.71 | 14.01 | 0.33 | 0.124 | 0.05 | 0.44 | 6.3 | 0.49 | 0.069 | 0.028 | 0.01 | 0.27 | stop | stop | stop | stop | stop | stop | 7.48 | 3060 |  | 114 | 0.12 |  | 0.67 | 7.23 | 2750 | 0.32 | 5.88 | 170.7 |  | 8
2026-09-16 | 5.61 | 14.28 | 0.24 | 0.15 | 0.06 | 3.642 | 0.4 | 6.15 | 0.57 | 0.012 | 0.02 | 0.01 | 0.27 | 0.22 | 0.26 | stop | stop | stop | stop | 6.27 | 789.4 | 0 | 0.3 | stop | stop | stop | stop | stop | stop | 5.16 | 14.41 | 0.23 | 0.139 | 0.03 | 0.5 | 6.28 | 0.57 | 0.028 | 0.012 | 0.03 | 0.23 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-17 | 5.81 | 14.87 | 0.21 | 0.114 | 0.02 | 3.642 | 0.23 | 6.56 | 0.72 | 0.083 | 0.116 | 0.03 | 0.38 | 0.38 | 0.2 | 6.2 | 1454 | 0 | 0.27 | stop | stop | stop | stop | 5.89 | 15.57 | 0.24 | 0.136 | 0.03 | 0.28 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.41 | 0.84 | 0.038 | 0.026 | 0.03 | 0.37 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-18 | 5.45 | 18.11 | 0.12 | 0.303 | 0.04 | 8.498 | 0.32 | 6.64 | 0.53 | 0.036 | 0.019 | 0.01 | 0.29 | 0.2 | 0.51 | 6.18 | 1025 | 0 | 0.5 | stop | stop | stop | stop | 5.4 | 18.32 | 0.14 | 0.296 | 0.02 | 0.26 | stop | stop | stop | stop | stop | stop | 6.58 | 0.62 | 0.037 | 0.026 | 0.01 | 0.25 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-19 | 5.99 | 21.13 | 0.17 | 0.404 | 0.02 | 4.856 | 0.53 | 6.51 | 0.56 | 0.067 | 0.022 | 0.01 | 0.75 | 0.25 | 0.32 | 6.28 | 882.5 | 0 | 0.21 | stop | stop | stop | stop | 5.6 | 21.63 | 0.44 | 0.344 | 0.01 | 0.21 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.53 | 0.5 | 0.022 | 0.016 | 0.02 | 0.29 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-20 | 5.81 | 17.82 | 0.31 | 0.421 | 0.02 | 3.642 | 0.27 | 6.56 | 0.9 | 0.048 | 0.028 | 0.01 | 0.43
2026-09-21 | 5.75 | 22.86 | 0.12 | 0.21 | 0.01 | 6.07 | 0.38 | 6.35 | 0.64 | 0.046 | 0.023 | 0.01 | 0.28 | 0.21 | 0.33 | 6.16 | 942.9 | 0 | 0.26 | stop | stop | stop | stop | 5.74 | 17.46 | 0.18 | 0.01 | 0.1 | 0.3 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.24 | 0.42 | 0.051 | 0.014 | 0.01 | 0.35 | 7.14 | 2690 | 254 | 142 | 0.14 | 694.26 | 1 | 6.88 | 3240 | 0.89 | 6.57 | 281 | 14 | 16 | 68.94
2026-09-22 | 5.42 | 16.43 | 0.17 | 0.34 | 0.02 | 5.03 | 0.31 | 6.77 | 0.69 | 0.022 | 0.027 | 0.02 | 0.3 | 0.4 | 0.21 | 6.16 | 820.4 | 0 | 0.37 | stop | stop | stop | stop | 5.4 | 19.14 | 0.41 | 0.353 | 0.03 | 0.23 | stop | stop | stop | stop | stop | stop | 6.75 | 0.56 | 0.059 | 0.023 | 0.02 | 0.4 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-23 | 5.94 | 23.14 | 0.46 | 0.384 | 0.04 | 8.498 | 0.21 | 6.56 | 0.51 | 0.038 | 0.046 | 0.03 | 0.35 | 0.34 | 0.61 | 6.2 | 1104 | 0 | 0.2 | stop | stop | stop | stop | 5.58 | 20.97 | 0.17 | 0.327 | 0.03 | 0.28 | stop | stop | stop | stop | stop | stop | 6.11 | 0.53 | 0.016 | 0.02 | 0.01 | 0.32 | stop | stop | stop | stop | stop | stop | 7.8 | 2730 | 250 | 144 | 0.11 | 773.55 | 0.41 | 7.22 | 3570 | 0.5 | 6.43 | 287.2 | 18 | 13 | 66.3
2026-09-24 | 5.83 | 18.1 | 0.19 | 0.378 | 0.03 | 6.07 | 0.39 | 6.57 | 0.67 | 0.049 | 0.04 | 0.02 | 0.29 | 0.3 | 0.26 | 6.29 | 800.7 | 0 | 0.36 | stop | stop | stop | stop | 5.68 | 13.29 | 0.14 | 0.231 | 0.02 | 0.26 | stop | stop | stop | stop | stop | stop | 6.46 | 0.63 | 0.038 | 0.05 | 0.01 | 0.33 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-25 | 5.82 | 16.51 | 0.37 | 0.152 | 0.02 | 3.642 | 0.39 | 6.77 | 0.44 | 0.045 | 0.011 | 0.01 | 0.24 | 0.48 | 0.24 | 6.3 | 814 | 0 | 0.15 | stop | stop | stop | stop | 5.87 | 13.19 | 0.17 | 0.166 | 0.02 | 0.22 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.35 | 0.28 | 0.041 | 0.008 | 0.01 | 0.25 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-26 | 5.95 | 15.42 | 0.36 | 0.184 | 0.02 | 3.642 | 0.44 | 6.2 | 0.64 | 0.014 | 0.013 | 0.01 | 0.43 | 0.2 | 0.84 | 6.18 | 517.7 | 0 | 0.34 | stop | stop | stop | stop | 5.6 | 11.64 | 0.02 | 0.169 | 0.01 | 0.43 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.4 | 0.4 | 0.091 | 0.009 | 0.02 | 0.41 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-27 | 5.49 | 13.22 | 0.25 | 0.412 | 0.01 | 3.642 | 0.22 | 6.47 | 0.29 | 0.038 | 0.011 | 0.02 | 0.22
2026-09-28 | 5.96 | 14.35 | 0.5 | 0.418 | 0.05 | 3.642 | 0.57 | 6.62 | 0.24 | 0.048 | 0.008 | 0.01 | 0.47 | 0.5 | 0.2 | stop | stop | stop | stop | 6.26 | 1030 | 0 | 0.19 | stop | stop | stop | stop | stop | stop | 5.32 | 17.05 | 0.21 | 0.333 | 0.01 | 0.81 | 6.37 | 0.29 | 0.023 | 0.006 | 0.01 | 0.24 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-29 | 5.74 | 18.19 | 0.32 | 0.362 | 0.01 | 4.856 | 0.36 | 6.83 | 0.65 | 0.01 | 0.013 | 0.01 | 0.39 | 0.31 | 0.31 | stop | stop | stop | stop | 6.34 | 1129 | 0 | 0.16 | stop | stop | stop | stop | stop | stop | 5.58 | 18.32 | 0.26 | 0.322 | 0.02 | 0.32 | 6.78 | 0.93 | 0.007 | 0.014 | 0.02 | 0.34 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-30 | 5.4 | 16.63 | 0.27 | 0.337 | 0.01 | 3.642 | 0.26 | 6.64 | 0.4 | 0.033 | 0.037 | 0.02 | 0.47 | 0.25 | 0.18 | stop | stop | stop | stop | 6.26 | 1066 | 0.01 | 0.2 | stop | stop | stop | stop | stop | stop | 5.38 | 16.47 | 0.24 | 0.332 | 0.01 | 0.26 | stop | stop | stop | stop | stop | stop | 6.82 | 0.4 | 0.052 | 0.026 | 0.01 | 0.37
2026-10-01
| RO TANK 600 MT | [6 empty] | DEMIN TANK BWRO | [5 empty] | RODEM #4A & RODEM #4B | [21 empty] | MIXBED | [11 empty] | RODOM #4 (BRINE #3)
[14 empty] | INLET SAND FILTER | OUTLET SAND FILTER | FEED RODEM #4A |  |  |  | FEED RODEM #4B |  |  |  | PERMEATE RO #4A | [5 empty] | PERMEATE RO #4B | [5 empty] | MB #5A | [5 empty] | MB #5B | [5 empty] | REJECT WATER TANK | [6 empty] | FEED RO After N- 7408 |  |  | PERMEATE RO RODOM #4
Parameter | pH | Conductivity | T. Hardness | Silica | Iron | Chloride | Chloride | pH | Conductivity | T. Hardness | Silica | Iron | Iron | Free Chlorine | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Chloride | Turbidity | pH | Conductivity | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride
|  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppmCl-) | (ppmCl-) |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppm Fe) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppmCl-) | NTU |  | (µS/cm) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-)
| 5.0 - 7.0 | < 50 | 1.5; Max | < 5 | < 0.10 | < 30 | < 30 | 5.5 - 7.0 | < 1.0 | 0.1; Max | 0.16 ; Max | 0.05 ; Max | 0.05 ; Max | 0.20 - 0.50 | N/A | 6.0 - 6.5 | < 1000 | < 0.10 | < 0.50 | 6.0 - 6.5 | < 1000 | < 0.10 | < 0.50 | 5.0 - 7.0 | < 50 | 1.5 : Max | < 5 | < 0.10 |  | 5.0 - 7.0 | < 50 | 1.5 : Max | < 5 | < 0.10 |  | 6.0 - 7.0 | 1.0 ; Max | 0.10; Max | 0.16 ; Max | 0.05 ; Max | <1 | 6.0 - 7.0 | 1.0 ; Max | 0.10; Max | 0.16 ; Max | 0.05 ; Max | <1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 6.0-6.5 | N/A | N/A | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A
2026-09-01 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop |  | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-02 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop |  | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-03 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop |  | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-04 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop |  | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
2026-09-05 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-06 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-07 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-08 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-09 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-10 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop |  | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-11 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop |  | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-12 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop |  | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-13 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-14 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop |  | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-15 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop |  | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | no data | 100% | 0% | 100% | 100% | 100% | 100% | no data | 100% | no data
2026-09-16 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop |  | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-17 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-18 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-19 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-20 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-21 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
2026-09-22 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-23 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
2026-09-24 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-25 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-26 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-27 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-28 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | stop | stop | stop | stop | 100% | 0% | 100% | 100% | stop | stop | stop | stop | stop |  | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-29 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | stop | stop | stop | stop | 100% | 0% | 100% | 100% | stop | stop | stop | stop | stop |  | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-30 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | stop | stop | stop | stop | 100% | 0% | 100% | 100% | stop | stop | stop | stop | stop |  | 100% | 100% | 100% | 100% | 100% |  | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-10-01 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
Conformance | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 76.92% | 100% | 100% | 100% | 76.92% | 100% | 100% | 100% | 100% |  | 100% |  |  | 100% | 100% |  | 100% |  |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
OVERALL VALUE
Date | DEMIN TANK | DYNALON #1 | MIXBED | DYNALON #2 | DYNALON #4
2026-09-01 | #REF! | 92.31% | #REF! | #REF! | #REF!
2026-09-02 | #REF! | 92.31% | #REF! | #REF! | #REF!
2026-09-03 | #REF! | 92.31% | #REF! | #REF! | #REF!
2026-09-04 | #REF! | 92.31% | #REF! | #REF! | #REF!
2026-09-05 | #REF! | 92.31% | #REF! | #REF! | #REF!
2026-09-06 | #REF! | 85.71% | #REF! | #REF! | #REF!
2026-09-07 | #REF! | 92.31% | #REF! | #REF! | #REF!
2026-09-08 | #REF! | 92.31% | #REF! | #REF! | #REF!
2026-09-09 | #REF! | 92.31% | #REF! | #REF! | #REF!
2026-09-10 | #REF! | 92.31% | #REF! | #REF! | #REF!
2026-09-11 | #REF! | 92.31% | #REF! | #REF! | #REF!
2026-09-12 | #REF! | 92.31% | #REF! | #REF! | #REF!
2026-09-13 | #REF! | 85.71% | #REF! | #REF! | #REF!
2026-09-14 | #REF! | 92.31% | #REF! | #REF! | #REF!
2026-09-15 | #REF! | 92.31% | #REF! | #REF! | #REF!
2026-09-16 | #REF! | 92.31% | #REF! | #REF! | #REF!
2026-09-17 | #REF! | 84.62% | #REF! | #REF! | #REF!
2026-09-18 | #REF! | 84.62% | #REF! | #REF! | #REF!
2026-09-19 | #REF! | 92.31% | #REF! | #REF! | #REF!
2026-09-20 | #REF! | 85.71% | #REF! | #REF! | #REF!
2026-09-21 | #REF! | 92.31% | #REF! | #REF! | #REF!
2026-09-22 | #REF! | 92.31% | #REF! | #REF! | #REF!
2026-09-23 | #REF! | 84.62% | #REF! | #REF! | #REF!
2026-09-24 | #REF! | 92.31% | #REF! | #REF! | #REF!
2026-09-25 | #REF! | 92.31% | #REF! | #REF! | #REF!
2026-09-26 | #REF! | 92.31% | #REF! | #REF! | #REF!
2026-09-27 | #REF! | 85.71% | #REF! | #REF! | #REF!
2026-09-28 | #REF! | 84.62% | #REF! | #REF! | #REF!
2026-09-29 | #REF! | 84.62% | #REF! | #REF! | #REF!
2026-09-30 | #REF! | 84.62% | #REF! | #REF! | #REF!
2026-10-01 | #REF! | no data | #REF! | #REF! | #REF!
Conformance |  | 89.89%
RO & MMF
2026-09-01
2026-09-02
2026-09-03
2026-09-04
2026-09-05
2026-09-06
2026-09-07
2026-09-08
2026-09-09
2026-09-10
2026-09-11
2026-09-12
2026-09-13
2026-09-14
2026-09-15
2026-09-16
2026-09-17
2026-09-18
2026-09-19
2026-09-20
2026-09-21
2026-09-22
2026-09-23
2026-09-24
2026-09-25
2026-09-26
2026-09-27
2026-09-28
2026-09-29
2026-09-30
2026-10-01

## RAW WATER
| RAW WATER | [6 empty] | RAW WATER | [6 empty] | RAW WATER | [6 empty] | RAW WATER | [6 empty] | RODOM #3 (DYNALON #3) | [16 empty] | RODOM #1 (BRINE #1) | [16 empty] | RODOM #2 (BRINE #2) | [16 empty] | RODOM #4 (BRINE #3)
| DOMESTIC TANK | [6 empty] | MIXING TANK | [6 empty] | RAW WATER TANK | [6 empty] | PDAM RESERVOAR | [6 empty] | REJECT WATER TANK | [6 empty] | FEED RO After biocide | FEED RO After N- 7408 |  |  |  | PERMEATE RODOM #3 |  |  |  |  | REJECT WATER TANK | [6 empty] | FEED RO After biocide | FEED RO After N- 7408 |  |  |  | PERMEATE RODOM #1 |  |  |  |  | REJECT WATER TANK | [6 empty] | FEED RO After biocide | FEED RO After N- 7408 |  |  |  | PERMEATE RODOM #2 |  |  |  |  | REJECT WATER TANK | [6 empty] | FEED RO After biocide | FEED RO After N- 7408 |  |  |  | PERMEATE RO RODOM #4
Parameter | pH | Conductivity | T. Hardness | Silica | Iron | Chloride | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Chloride | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Chloride | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Chloride | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Chloride | Turbidity | Free Chlorine | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | pH | Conductivity | T. Hardness | Silica | Iron | Chloride | Turbidity | Free Chlorine | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | pH | Conductivity | T. Hardness | Silica | Iron | Chloride | Turbidity | Free Chlorine | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | pH | Conductivity | T. Hardness | Silica | Iron | Chloride | Turbidity | Free Chlorine | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride
|  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppmCl-) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppmCl-) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppmCl-) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppmCl-) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppmCl-) | NTU | (ppm Cl2) |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppmCl-) | NTU | (ppm Cl2) |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppmCl-) | NTU | (ppm Cl2) |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppmCl-) | NTU | (ppm Cl2) |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-)
| 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | N/A | N/A | 6.5 - 8.0 | < 1000 | < 300 | N/A | N/A | N/A | N/A | 6.5 - 8.0 | < 1000 | < 300 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.20 - 0.50 | 6.0-6.5 | N/A | < 0.10 | N/A | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.20 - 0.50 | 6.0-6.5 | N/A | < 0.10 | N/A | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.20 - 0.50 | 6.0-6.5 | N/A | < 0.10 | N/A | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.20 - 0.50 | 6.0-6.5 | N/A | < 0.10 | N/A | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A
Date
2026-09-01 | 7.18 | 1632 | 142 | 71 | 0.07 | 483.9 | 0.52 | 7.4 | 817.7 | 108 | 23 | 0.44 | 181.35 | 3.25 | 7.58 | 650.3 | 104 | 36 | 0.64 | 119.18 | 4.8 | 7.49 | 262.7 | 102 | 57 | 0.02 | 5.12 | 0.53 | 7.3 | 2950 | 270 | 110 | 0.05 | 697.4 | 0.53 | 0.44 | 6.85 | 2980 | 0.01 | 0.34 | 5.98 | 784.5 | 84 | 46 | 185.02 | 7.3 | 2950 | 270 | 110 | 0.05 | 697.4 | 0.53 | 0.44 | 6.85 | 2980 | 0.01 | 0.34 | 5.98 | 784.5 | 84 | 46 | 185.02 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-02 | 7.42 | 1051 | 7 | 47 | 0.11 | 257.7 | 0.65 | 7.08 | 789.4 | 66 | 18 | 0.6 | 161 | 2.14 | 7.7 | 576.8 | 74 | 34 | 0.52 | 104.68 | 3.97 | 7.76 | 257.1 | 112 | 58 | 0.02 | 2.62 | 0.72 | 7.17 | 3390 | 164 | 28 | 0.04 | 921.95 | 0.31 | 0.44 | 6.13 | 3470 | 0 | 0.2 | 5.95 | 2390 | 118 | 46 | 490.8 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.17 | 3390 | 164 | 28 | 0.04 | 921.95 | 0.31 | 0.34 | 6.1 | 3480 | 0 | 0.31 | 5.66 | 424.9 | 36 | 8 | 106.65
2026-09-03 | 7.22 | 1462 | 108 | 55 | 0.42 | 407.36 | 1.83 | 7.122 | 724.7 | 60 | 15 | 0.73 | 57.34 | 4.53 | 7.58 | 566.3 | 64 | 25 | 0.19 | 103.54 | 1.94 | 7.4 | 264.7 | 114 | 28 | 0.02 | 3.33 | 1.64 | 7.08 | 2880 | 208 | 108 | 0.05 | 898 | 0.44 | 0.25 | 6.2 | 3070 | 0 | 0.33 | 5.98 | 2070 | 118 | 49 | 478.5 | 7.08 | 2880 | 208 | 108 | 0.05 | 898 | 0.44 | 0.24 | 6.2 | 3080 | 0 | 0.27 | 5.56 | 878.3 | 34 | 24 | 194.64 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-04 | 7.51 | 579.3 | 42 | 34 | 0.14 | 140.6 | 1.04 | 7.26 | 731.4 | 46 | 16 | 1 | 160.53 | 9.56 | 7.67 | 522 | 76 | 29 | 0.08 | 80.83 | 0.77 | 7.72 | 259 | 116 | 56 | 0.02 | 3.12 | 0.96 | 7.43 | 3010 | 212 | 126 | 0.09 | 736.05 | 0.3 | 0.2 | 6.49 | 3060 | 0 | 0.34 | 6.44 | 2190 | 172 | 76 | 494.5 | 7.43 | 3010 | 212 | 126 | 0.09 | 736.05 | 0.3 | 0.28 | 7.07 | 3000 | 0 | 0.41 | 6.07 | 844.2 | 44 | 39 | 188.9 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-05 | 7.51 | 696.4 | 80 | 25 | 0.13 | 153.3 | 0.57 | 7.37 | 774.3 | 44 | 13 | 0.16 | 168.94 | 1.15 | 7.58 | 552.9 | 80 | 27 | 0.8 | 99.45 | 7.64 | 7.64 | 266.8 | 112 | 49 | 0.02 | 7.27 | 0.87 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.19 | 2230 | 224 | 114 | 0.11 | 593.7 | 0.32 | 0.5 | 6.17 | 2880 | 0 | 0.32 | 6.04 | 762.4 | 48 | 25 | 175.94 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.19 | 2230 | 224 | 114 | 0.11 | 593.7 | 0.32 | 0.31 | 6.11 | 2880 | 0 | 0.46 | 5.53 | 453.9 | 32.9 | 9 | 121.89
2026-09-06
2026-09-07 | 6.86 | 710.2 | 66 | 39 | 0.33 | 182.82 | 2.4 | 7 | 682 | 46 | 20 | 1.25 | 160.09 | 11 | 6.99 | 500.4 | 70 | 35 | 0.08 | 96.31 | 0.91 | 7.74 | 238.5 | 100 | 56 | 0.02 | 3.69 | 0.91 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.38 | 2510 | 206 | 112 | 0.04 | 692.55 | 0.85 | 0.5 | 6.15 | 2580 | 0.01 | 0.3 | 6.61 | 929.8 | 62 | 43 | 248.42
2026-09-08 | 8.77 | 1266 | 90 | 56 | 0.09 | 346.81 | 0.75 | 7.12 | 614 | 52 | 24 | 0.54 | 130.4 | 3.22 | 7.15 | 589 | 60 | 31 | 0.18 | 115.41 | 1.98 | 7.32 | 349.8 | 90 | 59 | 0.01 | 10.14 | 0.47 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.4 | 2550 | 226 | 134 | 0.07 | 597.05 | 0.48 | 0.5 | 6.41 | 2610 | 0.02 | 0.39 | 5.99 | 1144 | 78 | 55 | 263.28
2026-09-09 | 6.9 | 1115 | 90 | 59 | 0.17 | 304 | 0.8 | 7.48 | 583 | 44 | 24 | 0.28 | 134.07 | 2.27 | 7.2 | 616.3 | 66 | 35 | 0.12 | 142.97 | 1.93 | 7.63 | 238.7 | 106 | 59 | 0.02 | 7.33 | 0.71 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.27 | 2630 | 228 | 118 | 0.04 | 770.95 | 0.29 | 0.49 | 6.48 | 2700 | 0.01 | 0.47 | 6.19 | 1291 | 80 | 50 | 357.58
2026-09-10 | 7.12 | 1186 | 98 | 58 | 0.11 | 343.54 | 0.49 | 7.36 | 549 | 54 | 21 | 1.68 | 132.61 | 4.78 | 7.48 | 624.3 | 70 | 29 | 0.04 | 154.83 | 2 | 7.4 | 221.7 | 104 | 60 | 0.02 | 6.65 | 1.56 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.35 | 2630 | 216 | 108 | 0.05 | 845.1 | 0.41 | 0.5 | 6.43 | 2750 | 0.01 | 0.44 | 6.19 | 1295 | 12 | 57 | 383.14
2026-09-11 | 7.08 | 1011 | 74 | 50 | 0.08 | 305.7 | 0.56 | 7.38 | 618.3 | 42 | 19 | 0.54 | 159.38 | 4.75 | 7.45 | 609.1 | 68 | 27 | 0.11 | 149.42 | 0.54 | 7.33 | 228 | 100 | 59 | 0.01 | 6.6 | 0.95 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-12 | 7.31 | 807.6 | 60 | 48 | 0.43 | 220.08 | 2.14 | 7.49 | 650.3 | 44 | 21 | 0.2 | 156.43 | 1.68 | 7.61 | 553.5 | 58 | 31 | 0.05 | 119.38 | 0.73 | 7.49 | 235.4 | 96 | 57 | 0.02 | 3.76 | 3.1 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.3 | 3480 | 336 | 90 | 0.04 | 1158.05 | 0.5 | 0.31 | 6.09 | 3410 | 0.01 | 0.23 | 5.92 | 1661 | 130 | 68 | 540.52
2026-09-13
2026-09-14 | 7.1 | 1258 | 96 | 50 | 0.82 | 397.14 | 4.41 | 7.23 | 691.4 | 70 | 22 | 0.88 | 186.23 | 5.36 | 7.55 | 666.7 | 64 | 23 | 0.27 | 170.83 | 2.28 | 7.56 | 215.1 | 138 | 53 | 0.02 | 3.92 | 0.47 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.21 | 2640 | 192 | 62 | 0.15 | 753.16 | 0.34 | 0.36 | 6.13 | 2680 | 0.01 | 0.27 | 5.7 | 1366 | 106 | 49 | 451.08
2026-09-15 | 7.35 | 1711 | 100 | 62 | 0.09 | 464.6 | 1.49 | 7.47 | 802.2 | 64 | 22 | 2.41 | 168.74 | 24 | 7.77 | 711.7 | 68 | 29 | 0.26 | 136.72 | 2.23 | 7.67 | 268.6 | 120 | 54 | 0.02 | 7.55 | 0.47 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.62 | 3310 | 230 | 126 | 0.19 | 796.78 | 0.87 | 0.45 | 6.3 | 3370 | 0.01 | 0.36 | 5.95 | 1819 | 126 | 71 | 475.9
2026-09-16 | 7.04 | 2370 | 140 | 63 | 0.12 | 520.48 | 1.36 | 7 | 790 | 50 | 20 | 1.89 | 181.46 | 17.8 | 7.56 | 679.5 | 80 | 33 | 0.46 | 117.67 | 2.41 | 7.42 | 258.2 | 126 | 52 | 0.03 | 10.92 | 0.44 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.42 | 3250 | 214 | 72 | 0.07 | 764.58 | 0.32 | 0.45 | 6.36 | 3330 | 0.01 | 0.47 | 5.95 | 2200 | 132 | 68 | 542.36
2026-09-17 | 6.83 | 2330 | 138 | 72 | 0.1 | 500.6 | 0.56 | 6.78 | 848.6 | 50 | 21 | 0.22 | 174.84 | 5.28 | 7.13 | 744.7 | 60 | 26 | 0.25 | 170.6 | 2.03 | 7.53 | 260 | 126 | 55 | 0.02 | 13.89 | 0.81 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.28 | 4140 | 322 | 106 | 0.08 | 976.48 | 0.2 | 0.22 | 6.14 | 3010 | 0 | 0.23 | 6.01 | 2930 | 206 | 80 | 758.22
2026-09-18 | 7.13 | 2660 | 156 | 71 | 0.2 | 744.44 | 1.26 | 7.24 | 820.57 | 70 | 25 | 0.92 | 170.06 | 11.8 | 7.53 | 870.8 | 76 | 32 | 0.28 | 199.21 | 1.93 | 7.66 | 262.1 | 116 | 53 | 0.03 | 2.61 | 0.6 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.18 | 3940 | 220 | 65 | 0.06 | 1005.78 | 0.45 | 0.28 | 6.18 | 3970 | 0 | 0.51 | 5.97 | 2930 | 156 | 69 | 521.62
2026-09-19 | 6.91 | 2570 | 156 | 70 | 0.09 | 609.3 | 0.55 | 7.19 | 818.5 | 76 | 20 | 0.54 | 185.57 | 1.81 | 7.4 | 785.5 | 100 | 26 | 1.09 | 174.28 | 2.92 | 7.25 | 264 | 118 | 55 | 0.02 | 5.84 | 0.36 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.23 | 3640 | 200 | 77 | 0.04 | 951.56 | 0.3 | 0.28 | 6.29 | 3730 | 0.01 | 0.27 | 6.08 | 2870 | 140 | 64 | 516.54
2026-09-20
2026-09-21 | 6.95 | 2980 | 144 | 68 | 0.54 | 827.58 | 3.47 | 7.36 | 886.5 | 38 | 17 | 0.01 | 224.93 | 2.52 | 7.67 | 771.1 | 50 | 29 | 0.14 | 179.8 | 1.1 | 7.26 | 282.6 | 96 | 59 | 0.02 | 3.99 | 0.5 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.1 | 3480 | 210 | 112 | 0.03 | 1027.25 | 0.31 | 0.5 | 6.39 | 3590 | 0.01 | 0.27 | 6.24 | 2800 | 154 | 96 | 840.9
2026-09-22 | 6.787 | 2970 | 148 | 80 | 0.08 | 882.8 | 0.76 | 7.38 | 811.2 | 40 | 20 | 0.4 | 195.59 | 4.13 | 7.66 | 664.6 | 54 | 31 | 0.76 | 149.31 | 6.78 | 7.22 | 255 | 94 | 61 | 0.02 | 6.94 | 0.99 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.58 | 3160 | 192 | 100 | 0.04 | 969.95 | 0.55 | 0.5 | 6.4 | 3280 | 0.01 | 0.39 | 6.38 | 2620 | 136 | 85 | 759.6
2026-09-23 | 7.09 | 2890 | 166 | 80 | 0.16 | 840.9 | 0.84 | 7.49 | 805.8 | 46 | 20 | 0.62 | 178.89 | 3.2 | 7.388 | 1112 | 88 | 29 | 0.15 | 268.07 | 0.89 | 7.4 | 261.7 | 96 | 58 | 0.01 | 7.73 | 0.83 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.18 | 4640 | 364 | 116 | 0.03 | 1376 | 0.7 | 0.35 | 6.35 | 4720 | 0 | 0.46 | 6.12 | 3900 | 274 | 90 | 1170.2
2026-09-24 | 6.98 | 3040 | 176 | 80 | 0.11 | 795.5 | 0.85 | 7.36 | 957.7 | 66 | 24 | 0.57 | 225.21 | 4.46 | 7.4 | 725.5 | 78 | 35 | 0.77 | 162.97 | 3.88 | 7.34 | 244.2 | 102 | 54 | 0.01 | 6.38 | 0.62 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.2 | 3440 | 224 | 80 | 0.03 | 1126.05 | 0.63 | 0.25 | 6.44 | 3480 | 0 | 0.44 | 6.23 | 2780 | 162 | 62 | 976.95
2026-09-25 | 7.18 | 2810 | 162 | 82 | 0.31 | 796.65 | 1.94 | 7.58 | 787.4 | 52 | 24 | 0.88 | 190.64 | 5.09 | 7.56 | 675.1 | 68 | 40 | 0.71 | 152.59 | 4.42 | 7.53 | 250.9 | 94 | 58 | 0.03 | 5.84 | 0.54 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.29 | 3300 | 256 | 126 | 0.07 | 947.7 | 0.41 | 0.27 | 6.48 | 3360 | 0 | 0.52 | 6.36 | 2660 | 180 | 102 | 806.15
2026-09-26 | 7.32 | 2300 | 158 | 82 | 0.16 | 622.3 | 0.88 | 7.6 | 774.5 | 60 | 24 | 0.29 | 194.95 | 1.56 | 7.08 | 508.2 | 68 | 39 | 0.37 | 99.37 | 1.86 | 7.64 | 258.6 | 96 | 61 | 0.02 | 4.89 | 0.7 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.34 | 24600 | 260 | 148 | 0.03 | 777.86 | 0.9 | 0.29 | 6.2 | 2620 | 0 | 0.34 | 6.1 | 1925 | 180 | 124 | 617.84
2026-09-27
2026-09-28 | 7.51 | 1946 | 180 | 73 | 0.98 | 553.82 | 7.7 | 7.5 | 551.5 | 80 | 27 | 1.28 | 126.78 | 7.75 | 7.61 | 957.2 | 96 | 32 | 0.04 | 258.91 | 0.45 | 7.25 | 220.7 | 128 | 57 | 0.03 | 3.09 | 0.7 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.43 | 3620 | 306 | 81 | 0.04 | 1297.7 | 0.4 | 0.46 | 6.5 | 3690 | 0 | 0.48 | 6.38 | 3090 | 258 | 80 | 954
2026-09-29 | 7.5 | 2150 | 134 | 65 | 0.24 | 655.9 | 1.38 | 7.3 | 942.5 | 60 | 14 | 0.61 | 242.33 | 5.28 | 7.59 | 1087 | 106 | 42 | 0.15 | 276.8 | 0.69 | 7.67 | 235.4 | 106 | 54 | 0.01 | 3.9 | 0.39 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.8 | 3500 |  | 82 | 0.04 |  | 0.4 | 0.44 | 6.5 | 3510 | 0 | 0.35 | 6.44 | 2930 |  | 80
2026-09-30 | 7.51 | 2960 | 209 | 67 | 0.16 | 847.85 | 0.97 | 7.44 | 785.5 | 59.2 | 21 | 0.36 | 188.73 | 2.22 | 7.61 | 966.9 | 77.8 | 34 | 0.3 | 235.77 | 1.24 | 7.61 | 233.9 | 121.4 | 59 | 0.01 | 3.42 | 0.67
2026-10-01
RAW WATER | [7 empty] | RAW WATER | [6 empty] | RAW WATER | [6 empty] | RAW WATER | [6 empty] | RODOM #3 (DYNALON #3) | [16 empty] | RODOM #1 (BRINE #1) | [16 empty] | RODOM #2 (BRINE #2) | [16 empty] | RODOM #4 (BRINE #3)
DOMESTIC TANK | [7 empty] | MIXING TANK | [6 empty] | RAW WATER TANK | [6 empty] | PDAM RESERVOAR | [6 empty] | REJECT WATER TANK | [6 empty] | FEED RO After biocide | FEED RO After N- 7408 |  |  |  | PERMEATE RODOM #3 |  |  |  |  | REJECT WATER TANK | [6 empty] | FEED RO After biocide | FEED RO After N- 7408 |  |  |  | PERMEATE RODOM #1 |  |  |  |  | REJECT WATER TANK | [6 empty] | FEED RO After biocide | FEED RO After N- 7408 |  |  |  | PERMEATE RODOM #2 |  |  |  |  | RODOM #4 (BRINE #3) | [6 empty] | FEED RO After biocide | FEED RO After N- 7408 |  |  |  | PERMEATE RO RODOM #4
Parameter | pH | Conductivity | T. Hardness | Silica | Iron | Chloride | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Chloride | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Chloride | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Chloride | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Chloride | Turbidity | Free Chlorine | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | pH | Conductivity | T. Hardness | Silica | Iron | Chloride | Turbidity | Free Chlorine | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | pH | Conductivity | T. Hardness | Silica | Iron | Chloride | Turbidity | Free Chlorine | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | pH | Conductivity | T. Hardness | Silica | Iron | Chloride | Turbidity | Free Chlorine | pH | Conductivity | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride
|  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppmCl-) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppmCl-) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppmCl-) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppmCl-) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppmCl-) | NTU | (ppm Cl2) |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppmCl-) | NTU | (ppm Cl2) |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppmCl-) | NTU | (ppm Cl2) |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppmCl-) | NTU | (ppm Cl2) |  | (µS/cm) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-)
| 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | N/A | N/A | 6.5 - 8.0 | < 1000 | < 300 | N/A | N/A | N/A | N/A | 6.5 - 8.0 | < 1000 | < 300 | N/A | N/A | N/A | N/A | 6.5 - 8.0 | < 700 | < 300 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.20 - 0.50 | 6.0-6.5 | N/A | < 0.10 | N/A | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.20 - 0.50 | 6.0-6.5 | N/A | < 0.10 | N/A | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.20 - 0.50 | 6.0-6.5 | N/A | < 0.10 | N/A | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.20 - 0.50 | 6.0-6.5 | N/A | < 0.10 | N/A | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A
2026-09-01 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-02 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
2026-09-03 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-04 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-05 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
2026-09-06 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-07 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
2026-09-08 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100%
2026-09-09 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100%
2026-09-10 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100%
2026-09-11 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-12 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100%
2026-09-13 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-14 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100%
2026-09-15 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100%
2026-09-16 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100%
2026-09-17 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100%
2026-09-18 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100%
2026-09-19 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100%
2026-09-20 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-21 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100%
2026-09-22 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100%
2026-09-23 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100%
2026-09-24 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100%
2026-09-25 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100%
2026-09-26 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100%
2026-09-27 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-28 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100%
2026-09-29 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | no data | 100% | no data
2026-09-30 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-10-01 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
CONFORMANCE | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 92.31% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 75% | 100% | 100% | 100% | 100% | 25% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 50% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | [17 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 14.29% | 100% | 100% | 100%
OVERALL VALUE
Date | DOMESTIC TANK | MIXING TANK | RAW WATER TANK | PDAM | DYNALON #3 | RO BRINE #1 | RO BRINE #2 | RO BRINE #3
2026-09-01 | 100% | 100% | 100% | 100% | 94.12% | 94.12% | stop | stop
2026-09-02 | 100% | 100% | 100% | 100% | 94.12% | stop | stop | 100%
2026-09-03 | 100% | 100% | 100% | 100% | 94.12% | 100% | stop | stop
2026-09-04 | 100% | 100% | 100% | 100% | 94.12% | 94.12% | stop | stop
2026-09-05 | 100% | 100% | 100% | 100% | stop | 100% | stop | 100%
2026-09-06 | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-07 | 100% | 100% | 100% | 100% | stop | stop | stop | 100%
2026-09-08 | 100% | 100% | 100% | 100% | stop | stop | stop | 94.12%
2026-09-09 | 100% | 100% | 100% | 100% | stop | stop | stop | 94.12%
2026-09-10 | 100% | 100% | 100% | 100% | stop | stop | stop | 94.12%
2026-09-11 | 100% | 100% | 100% | 100% | stop | stop | stop | stop
2026-09-12 | 100% | 100% | 100% | 100% | stop | stop | stop | 94.12%
2026-09-13 | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-14 | 100% | 100% | 100% | 100% | stop | stop | stop | 94.12%
2026-09-15 | 100% | 100% | 100% | 100% | stop | stop | stop | 94.12%
2026-09-16 | 100% | 100% | 100% | 100% | stop | stop | stop | 94.12%
2026-09-17 | 100% | 100% | 100% | 100% | stop | stop | stop | 94.12%
2026-09-18 | 100% | 100% | 100% | 100% | stop | stop | stop | 94.12%
2026-09-19 | 100% | 100% | 100% | 100% | stop | stop | stop | 94.12%
2026-09-20 | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-21 | 100% | 100% | 100% | 100% | stop | stop | stop | 94.12%
2026-09-22 | 100% | 100% | 100% | 100% | stop | stop | stop | 94.12%
2026-09-23 | 100% | 100% | 85.71% | 100% | stop | stop | stop | 94.12%
2026-09-24 | 100% | 100% | 100% | 100% | stop | stop | stop | 94.12%
2026-09-25 | 100% | 100% | 100% | 100% | stop | stop | stop | 94.12%
2026-09-26 | 100% | 100% | 100% | 100% | stop | stop | stop | 94.12%
2026-09-27 | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-28 | 100% | 100% | 100% | 100% | stop | stop | stop | 94.12%
2026-09-29 | 100% | 100% | 85.71% | 100% | stop | stop | stop | 92.31%
2026-09-30 | 100% | 100% | 100% | 100% | no data | no data | no data | no data
2026-10-01 | no data | no data | no data | no data | no data | no data | no data | no data
Conformance | 100% | 100% | 98.9% | 100% | 94.12% | 97.06% |  | 94.87%
RAW WATER
2026-09-01 | 98.04%
2026-09-02 | 99.02%
2026-09-03 | 99.02%
2026-09-04 | 98.04%
2026-09-05 | 100%
2026-09-06
2026-09-07 | 100%
2026-09-08 | 98.82%
2026-09-09 | 98.82%
2026-09-10 | 98.82%
2026-09-11 | 100%
2026-09-12 | 98.82%
2026-09-13
2026-09-14 | 98.82%
2026-09-15 | 98.82%
2026-09-16 | 98.82%
2026-09-17 | 98.82%
2026-09-18 | 98.82%
2026-09-19 | 98.82%
2026-09-20
2026-09-21 | 98.82%
2026-09-22 | 98.82%
2026-09-23 | 95.97%
2026-09-24 | 98.82%
2026-09-25 | 98.82%
2026-09-26 | 98.82%
2026-09-27
2026-09-28 | 98.82%
2026-09-29 | 95.6%
2026-09-30 | 100%
2026-10-01

## SWRO
| INTAKE SWRO |  | SWRO #1 | [27 empty] | FEED SWRO #2 | [28 empty] | SWRO #3 | [28 empty] | SWRO #4 | [12 empty] | SWRO #5 | [37 empty] | PRODUCT SWRO
| INTAKE 1 | INTAKE 2 | INLET DAF |  |  |  | OUTLET DAF |  | INLET MMF | OUTLET MMF |  | FEED WATER | [6 empty] | PERMEATE R/O #1A | [5 empty] | PERMEATE R/O #1B | [5 empty] | INLET DAF |  |  |  | OUTLET DAF |  |  | INLET MMF | OUTLET MMF |  | FEED WATER | [6 empty] | PERMEATE R/O #2A | [5 empty] | PERMEATE R/O #2B | [5 empty] | INLET DAF |  |  |  | OUTLET DAF |  |  | INLET MMF | OUTLET MMF |  | FEED WATER | [6 empty] | PERMEATE R/O #3A | [5 empty] | PERMEATE R/O #3B | [5 empty] | FEED WATER | [6 empty] | PERMEATE R/O #4 | [5 empty] | INLET DAF |  |  |  | OUTLET DAF | [5 empty] | INLET MMF | OUTLET MMF |  | FEED WATER | [6 empty] | PERMEATE R/O #5A | [5 empty] | PERMEATE R/O #5B | [5 empty] | PERMEATE R/O #5C | [5 empty] | PERMEATE SWRO #1 |  |  |  | PERMEATE SWRO #2,#3,#4 |  |  |  | PERMEATE SWRO #5
Parameter | Turbidity | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | Turbidity DAF 1 | Turbidity DAF 2 | Turbidity | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | Turbidity DAF 1 | Turbidity DAF 2 | Turbidity DAF 3 | Turbidity | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | Turbidity DAF 1 | Turbidity DAF 2 | Turbidity DAF 3 | Turbidity | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | Turbidity DAF 1 | Turbidity DAF 2 | Turbidity DAF 3 | Turbidity DAF 4 | Turbidity DAF 5 | Turbidity DAF 6 | Turbidity | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | Turbidity | pH | Conductivity | Iron | Turbidity | pH | Conductivity | Iron | Turbidity | pH | Conductivity | Iron | Turbidity
| NTU | NTU |  | (µS/cm) | (ppm Cl2) | NTU | NTU | NTU | NTU | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) | NTU |  | (µS/cm) | (ppm Cl2) | NTU | NTU | NTU | NTU | NTU | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) | NTU |  | (µS/cm) | (ppm Cl2) | NTU | NTU | NTU | NTU | NTU | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) | NTU |  | (µS/cm) | (ppm Cl2) | NTU | NTU | NTU | NTU | NTU | NTU | NTU | NTU | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) | NTU |  | (µS/cm) | (ppm Fe) | NTU |  | (µS/cm) | (ppm Fe) | NTU |  | (µS/cm) | (ppm Fe) | NTU
| N/A | N/A | N/A | N/A | 0.2 - 0.5 | N/A | < 5 | < 5 | < 5 | N/A | < 1 | 6.0 - 6.5 | N/A | N/A | N/A | max 0.05 | < 0.05 | < 0.5 | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | <1 | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | <1 | N/A | N/A | 0.2 - 0.5 | N/A | < 5 | < 5 | < 5 | < 5 | N/A | < 1 | 6.0 - 6.5 | N/A | N/A | N/A | max 0.05 | < 0.05 | < 0.5 | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | <1 | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | <1 | N/A | N/A | 0.2 - 0.5 | N/A | < 5 | < 5 | < 5 | < 5 | N/A | < 1 | 6.0 - 6.5 | N/A | N/A | N/A | max 0.05 | < 0.05 | < 0.5 | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | <1 | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | <1 | 6.0 - 6.5 | N/A | N/A | N/A | max 0.05 | < 0.05 | < 0.5 | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | N/A | N/A | N/A | 0.2 - 0.5 | N/A | < 5 | < 5 | < 5 | < 5 | < 5 | < 5 | < 5 | N/A | < 1 | 6.0 - 6.5 | N/A | N/A | N/A | max 0.05 | < 0.05 | < 0.5 | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | <1 | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | <1 | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | N/A | 6.5 - 7.5 | < 1000 | N/A | <1 | 6.5 - 7.5 | < 1000 | N/A | <1 | 6.5 - 7.5 | < 1000 | N/A | <1
2026-09-01 | 13.9 | 48.4 | 7.34 | 63400 | 0.32 | 41.7 | 3.99 | 3.57 | 3.96 | 0.21 | 0.83 | 6.2 | 54800 | 7280 | 1 | 0.02 | 0 | 0.43 | 5.51 | 549.5 | 2 | 0.022 | 134.8 | 0.4 | 5.42 | 626.7 | 4 | 0.015 | 150 | 0.33 | 7.18 | 63700 | 0.27 | 53.5 | 5.36 | stop | stop | 6.55 | 0.09 | 0.55 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.22 | 63800 | 0.24 | 49.4 | 3.54 | 3.63 | 3.46 | 5.96 | 0.26 | 0.62 | 6.17 | 45100 | 8200 | 2 | 0.01 | 0 | 0.46 | stop | stop | stop | stop | stop | stop | 5.58 | 737.1 | 4 | 0.016 | 226.42 | 0.44 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.58 | 64100 | 0.26 | 50.6 | 5.92 | 5.75 | 5.33 | stop | 5.68 | stop | 6.57 | 0.17 | 0.72 | 6.32 | 54100 | 6360 | 1 | 0.01 | 0 | 0.5 | stop | stop | stop | stop | stop | stop | 5.51 | 1522 | 12 | 0.029 | 402.04 | 0.39 | 5.62 | 1553 | 14 | 0.029 | 423.84 | 0.4 | 6.8 | 614.3 | 0.06 | 0.53 | 6.54 | 1469 | 0.07 | 0.52 | 6.58 | 1486 | 0.012 | 0.48
2026-09-02 | 20.1 | 14.4 | 7.54 | 61110 | 0.31 | 16.9 | 3.74 | 3.67 | 4 | 0.08 | 0.8 | 6.24 | 62200 | 8680 | 1 | 0.02 | 0 | 0.46 | 5.49 | 576.7 | 2 | 0.024 | 144.61 | 0.41 | 5.4 | 623.9 | 4 | 0.026 | 149.91 | 0.24 | 7.53 | 61700 | 0.27 | 47.8 | 5.81 | 5.58 | 5.85 | 6.75 | 0.08 | 0.66 | 6.2 | 63800 | 9320 | 1 | 0.01 | 0 | 0.48 | stop | stop | stop | stop | stop | stop | 5.44 | 555.9 | 4 | 0.029 | 138.64 | 0.47 | 7.51 | 61500 | 0.27 | 38.4 | 3.46 | 3.51 | 3.57 | 5.87 | 0.07 | 0.65 | 6.23 | 63100 | 7840 | 2 | 0.02 | 0 | 0.42 | 5.36 | 718.4 | 4 | 0.025 | 174.29 | 0.19 | 5.56 | 711.2 | 4 | 0.018 | 179.66 | 0.26 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.78 | 61100 | 0.23 | 35.6 | 3.44 | 3.83 | 4.35 | stop | 3.47 | stop | 5.56 | 0.07 | 0.69 | 6.28 | 62600 | 8400 | 1 | 0.01 | 0 | 0.41 | 5.21 | 1320 | 10 | 0.04 | 349.14 | 0.23 | 5.49 | 1529 | 12 | 0.032 | 413.12 | 0.18 | 5.61 | 1611 | 16 | 0.04 | 461.22 | 0.19 | 6.88 | 616.1 | 0.07 | 0.52 | 6.67 | 1194 | 0.09 | 0.34 | 6.53 | 1495 | 0.08 | 0.48
2026-09-03 | 9.92 | 13.4 | 7.15 | 62200 | 0.5 | 19.7 | 3.42 | 3.44 | 3.99 | 0.12 | 0.87 | 6.22 | 61800 | 6240 | 1 | 0.02 | 0 | 0.48 | 5.84 | 623 | 2 | 0.026 | 155.53 | 0.47 | 5.63 | 553.4 | 2 | 0.077 | 131.5 | 0.41 | 7.25 | 61900 | 0.5 | 35.5 | 6.07 | 5.79 | 6.14 | 6.79 | 0.04 | 0.87 | 6.25 | 63500 | 9080 | 1 | 0.01 | 0 | 0.5 | stop | stop | stop | stop | stop | stop | 5.62 | 567.9 | 4 | 0.043 | 139.2 | 0.41 | 7.28 | 61800 | 0.3 | 33.8 | 3.35 | 3.3 | 3.86 | 5.7 | 0.11 | 0.81 | 6.26 | 63300 | 6880 | 1 | 0.01 | 0 | 0.48 | 5.82 | 747.6 | 4 | 0.026 | 185.18 | 0.47 | 5.88 | 732.8 | 4 | 0.036 | 180.25 | 0.46 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.87 | 61100 | 0.3 | 37.3 | 3.84 | stop | 3.53 | stop | 3.86 | stop | 5.71 | 0.12 | 0.84 | 6.39 | 62600 | 8840 | 1 | 0.09 | 0 | 0.49 | 5.56 | 1318 | 10 | 0.029 | 338.85 | 0.45 | 5.58 | 1624 | 14 | 0.042 | 446.45 | 0.47 | 5.9 | 1528 | 14 | 0.041 | 403.15 | 0.45 | 7.11 | 634.2 | 0.03 | 0.35 | 7.06 | 980.2 | 0.01 | 0.48 | 6.75 | 1515 | 0.09 | 0.39
2026-09-04 | 10.7 | 17.3 | 6.95 | 59500 | 0.41 | 18.8 | 3.44 | 3.76 | 3.93 | 0.01 | 0.85 | 6.14 | 61300 | 7800 | 1 | 0.02 | 0 | 0.44 | 5.53 | 580.4 | 2 | 0.019 | 145.23 | 0.41 | stop | stop | stop | stop | stop | stop | 7.07 | 59800 | 0.43 | 43.6 | 5.8 | 5.67 | 6.26 | 6.3 | 0.04 | 0.9 | 6.17 | 62200 | 8200 | 1 | 0.02 | 0 | 0.47 | stop | stop | stop | stop | stop | stop | 5.35 | 559.3 | 4 | 0.015 | 137.69 | 0.32 | 7.07 | 59900 | 0.28 | 37.5 | 3.85 | 3.24 | 3.64 | 5.57 | 0.01 | 0.91 | 6.3 | 62100 | 8460 | 1 | 0.02 | 0 | 0.46 | 5.91 | 728.7 | 4 | 0.017 | 183.17 | 0.42 | 5.83 | 743.5 | 4 | 0.015 | 186.83 | 0.19 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.86 | 60500 | 0.44 | 39.7 | 4.61 | stop | 4.6 | stop | 4.3 | stop | 5.76 | 0.03 | 0.89 | 6.42 | 61400 | 8300 | 1 | 0.05 | 0 | 0.48 | 5.41 | 1182 | 10 | 0.025 | 308.38 | 0.26 | 5.5 | 1528 | 14 | 0.026 | 406.26 | 0.24 | 5.71 | 1671 | 16 | 0.034 | 450.62 | 0.29 | 7.42 | 603.4 | 0.15 | 0.56 | 7.31 | 1044 | 0.01 | 0.43 | 6.9 | 1453 | 0.02 | 0.68
2026-09-05 | 11.5 | 66.2 | 6.86 | 64000 | 0.23 | 19.9 | 3.98 | 3.81 | 4 | 0.01 | 0.69 | 6.26 | 64800 | 7780 | 1 | 0.03 | 0 | 0.49 | 5.49 | 577.6 | 2 | 0.024 | 139.24 | 0.48 | stop | stop | stop | stop | stop | stop | 6.88 | 64100 | 0.33 | 36.7 | 5.5 | 4.43 | 4.66 | 6.35 | 0.03 | 0.75 | 6.38 | 64900 | 8120 | 1 | 0.01 | 0 | 0.5 | 5.54 | 722.5 | 4 | 0.022 | 169.12 | 0.47 | 5.47 | 526 | 2 | 0.018 | 129.84 | 0.48 | 6.88 | 64200 | 0.2 | 31.3 | 2.95 | 3.07 | 3.25 | 5.48 | 0.02 | 0.75 | 6.43 | 65100 | 7900 | 1 | 0.01 | 0 | 0.47 | 5.57 | 774.8 | 4 | 0.024 | 186.34 | 0.45 | 5.68 | 767.4 | 4 | 0.019 | 188.23 | 0.46 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.84 | 63800 | 0.44 | 34.5 | 4.05 | stop | 3.99 | stop | 4.18 | stop | 5.54 | 0.03 | 0.83 | 6.45 | 64000 | 6980 | 1 | 0.05 | 0 | 0.44 | 5.34 | 1238 | 12 | 0.025 | 326.98 | 0.4 | 5.36 | 1595 | 14 | 0.036 | 428.04 | 0.43 | 5.63 | 1744 | 16 | 0.03 | 458.22 | 0.3 | 7.26 | 631.6 | 0.03 | 0.34 | 7.5 | 784.7 | 0.09 | 0.32 | 7.06 | 1443 | 0.04 | 0.51
2026-09-06
2026-09-07 | 6.44 | 35.2 | 7.07 | 63200 | 0.4 | 21.9 | 3.83 | 4.32 | 4.9 | 0.04 | 0.61 | 6.18 | 65600 | 7360 | 1 | 0.03 | 0 | 0.45 | 5.38 | 568.5 | 8 | 0.033 | 154.02 | 0.38 | 5.36 | 766 | 4 | 0.023 | 201.92 | 0.37 | 7.09 | 63400 | 0.49 | 27.4 | 5.74 | 5.96 | 6.59 | 6.98 | 0.08 | 0.84 | 6.24 | 66000 | 8400 | 1 | 0.03 | 0 | 0.5 | 5.59 | 688.7 | 8 | 0.042 | 186.07 | 0.4 | 5.64 | 503 | 6 | 0.017 | 132.42 | 0.42 | 7.15 | 63900 | 0.35 | 32.3 | 4.28 | 4.13 | 4.01 | 5.98 | 0.03 | 0.89 | 6.28 | 66100 | 8440 | 1 | 0.04 | 0 | 0.49 | stop | stop | stop | stop | stop | stop | 5.48 | 753.7 | 10 | 0.038 | 212.83 | 0.43 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.71 | 63500 | 0.48 | 37.4 | 4.37 | 6.19 | 4.4 | stop | 4.93 | stop | 6.12 | 0.71 | 0.99 | 6.36 | 65500 | 8200 | 1 | 0.04 | 0 | 0.49 | 5.28 | 1112 | 16 | 0.028 | 356.85 | 0.4 | 5.42 | 1422 | 20 | 0.022 | 458.05 | 0.42 | stop | stop | stop | stop | stop | stop | 6.52 | 666.4 | 0.11 | 1.07 | 6.8 | 1157 | 0.12 | 1.05 | 6.6 | 1265 | 0.1 | 1.29
2026-09-08 | 5.56 | 15.8 | 6.92 | 57400 | 0.25 | 20.3 | 3.84 | 4.38 | 4.96 | 0.22 | 0.3 | 6.2 | 58900 | 9040 | 1 | 0.04 | 0 | 0.3 | 5.42 | 605.2 | 8 | 0.02 | 151.2 | 0.2 | 5.4 | 774 | 8 | 0.006 | 209.44 | 0.21 | 6.84 | 58300 | 0.4 | 24.4 | 5.72 | 5.23 | 6.55 | 6.95 | 0.06 | 0.6 | 6.19 | 57800 | 8920 | 1 | 0.05 | 0 | 0.37 | stop | stop | stop | stop | stop | stop | 5.68 | 596.1 | 6 | 0.012 | 155.94 | 0.22 | 6.97 | 58000 | 0.43 | 32.7 | 3.29 | 3.56 | 3.55 | 5.95 | 0.05 | 0.55 | 6.25 | 58100 | 6200 | 1 | 0.03 | 0 | 0.37 | 5.78 | 730.5 | 8 | 0.017 | 198.26 | 0.19 | 5.69 | 764.7 | 8 | 0.016 | 197.36 | 0.2 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.33 | 58300 | 9000 | 1 | 0.05 | 0 | 0.4 | 5.56 | 1164 | 16 | 0.023 | 312.3 | 0.2 | 5.6 | 1507 | 20 | 0.27 | 467.95 | 0.22 | stop | stop | stop | stop | stop | stop | 6.7 | 948.5 | 0.1 | 0.95 | 6.52 | 1199 | 0.1 | 0.95 | 6.61 | 1358 | 0.17 | 1.08
2026-09-09 | 7.12 | 17.7 | 7.32 | 54100 | 0.23 | 38.3 | 4.24 | 3.67 | 4.93 | 0.19 | 0.51 | 6.17 | 53500 | 7440 | 1 | 0.01 | 0 | 0.4 | 5.7 | 571.6 | 4 | 0.032 | 152.67 | 0.24 | 5.31 | 714.7 | 4 | 0.03 | 200.08 | 0.26 | 7.05 | 51900 | 0.24 | 47.6 | 5.48 | 5.53 | 5.85 | 6.76 | 0.14 | 0.73 | 6.24 | 52300 | 8320 | 1 | 0.03 | 0 | 0.44 | stop | stop | stop | stop | stop | stop | 5.55 | 549 | 6 | 0.014 | 150.53 | 0.31 | 7.03 | 51600 | 0.2 | 33.5 | 3.79 | 3.78 | 3.98 | 5.9 | 0.16 | 0.81 | 6.21 | 52100 | 8120 | 1 | 0.02 | 0 | 0.43 | 5.66 | 703.8 | 6 | 0.017 | 192.33 | 0.33 | 5.73 | 733 | 4 | 0.01 | 205.47 | 0.35 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.25 | 51900 | 8560 | 1 | 0.07 | 0 | 0.49 | 5.32 | 1231 | 18 | 0.016 | 370.4 | 0.29 | 5.49 | 1343 | 12 | 0.016 | 401.4 | 0.33 | stop | stop | stop | stop | stop | stop | 6.78 | 963 | 0.12 | 2.7 | 6.69 | 1249 | 0.08 | 0.8 | 6.71 | 1308 | 0.1 | 0.65
2026-09-10 | 4.45 | 31.8 | 7.56 | 51800 | 0.2 | 17.3 | 4.81 | 3.72 | 4.98 | 0.16 | 0.57 | 6.11 | 52400 | 7200 | 1 | 0.02 | 0 | 0.44 | 5.56 | 543.7 | 8 | 0.03 | 153.65 | 0.29 | 5.5 | 638.7 | 2 | 0.029 | 181.64 | 0.24 | 7.38 | 50800 | 0.2 | 25.5 | 6.54 | 6.58 | 6.41 | 6.9 | 0.07 | 0.88 | 6.2 | 51800 | 6200 | 1 | 0.05 | 0 | 0.48 | stop | stop | stop | stop | stop | stop | 5.52 | 516.7 | 6 | 0.037 | 140.79 | 0.36 | 7.41 | 50100 | 0.21 | 37.4 | 3.24 | 4.1 | 3.52 | 5.75 | 0.07 | 0.76 | 6.3 | 51600 | 7760 | 1 | 0.05 | 0 | 0.47 | 5.55 | 672 | 6 | 0.035 | 199 | 0.3 | 5.66 | 724.4 | 6 | 0.033 | 211.6 | 0.3 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.24 | 51400 | 9400 | 1 | 0.02 | 0 | 0.49 | 5.5 | 1132 | 20 | 0.03 | 418.4 | 0.33 | 5.56 | 1274 | 14 | 0.04 | 457.05 | 0.29 | stop | stop | stop | stop | stop | stop | 6.73 | 614.5 | 0.38 | 3.44 | 6.65 | 1269 | 0.1 | 1.03 | 6.77 | 1271 | 0.7 | 0.94
2026-09-11 | 10.5 | 21.5 | 6.97 | 51600 | 0.2 | 17.3 | 4.54 | 4.26 | 4.9 | 0.21 | 0.8 | 6.15 | 53000 | 7840 | 1 | 0.03 | 0 | 0.46 | 5.54 | 542 | 8 | 0.038 | 151.87 | 0.35 | 5.48 | 629.5 | 8 | 0.037 | 187.23 | 0.33 | 6.93 | 51500 | 0.2 | 26.2 | 5.94 | 5.59 | 5.53 | 6.8 | 0.07 | 0.86 | 6.23 | 52000 | 7440 | 1 | 0.05 | 0 | 0.5 | stop | stop | stop | stop | stop | stop | 5.58 | 551.3 | 6 | 0.069 | 165.28 | 0.3 | 6.67 | 51600 | 0.2 | 34.6 | 4.64 | 4.1 | 3.95 | 5.98 | 0.09 | 0.9 | 6.27 | 52400 | 8520 | 1 | 0.05 | 0 | 0.5 | 5.6 | 705.1 | 6 | 0.024 | 202.39 | 0.3 | 5.64 | 726 | 6 | 0.022 | 225.64 | 0.33 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.58 | 51600 | 0.2 | 29.4 | stop | 4.58 | 4.5 | stop | 5.86 | stop | 6.98 | 0.07 | 1.2 | 6.33 | 52400 | 7960 | 1 | 0.03 | 0 | 0.49 | 5.47 | 1119 | 12 | 0.031 | 345.3 | 0.35 | 5.5 | 1325 | 12 | 0.043 | 435.85 | 0.31 | stop | stop | stop | stop | stop | stop | 6.61 | 648.3 | 0.09 | 1.3 | 6.58 | 1201 | 0.05 | 0.63 | 6.58 | 1237 | 0.07 | 0.76
2026-09-12 | 16.6 | 18.1 | 6.72 | 50600 | 0.2 | 20.1 | 4.14 | 3.66 | 4.93 | 0.12 | 0.57 | 6.1 | 53300 | 8300 | 2 | 0.04 | 0 | 0.4 | 5.26 | 575 | 6 | 0.036 | 184.25 | 0.25 | 5.36 | 679.5 | 4 | 0.019 | 218.48 | 0.24 | 6.91 | 51000 | 0.21 | 25.3 | 6.21 | 5.93 | 5.66 | 6.62 | 0.12 | 0.8 | 6.17 | 53300 | 8500 | 2 | 0.01 | 0 | 0.48 | stop | stop | stop | stop | stop | stop | 5.28 | 564.7 | 2 | 0.019 | 156.04 | 0.31 | 6.84 | 51100 | 0.46 | 35.2 | 4.34 | 4.09 | 3.94 | 5.9 | 0.01 | 0.87 | 6.34 | 53000 | 7700 | 2 | 0.01 | 0 | 0.49 | 5.53 | 760.3 | 4 | 0.024 | 225.86 | 0.26 | 5.59 | 782 | 4 | 0.01 | 205.94 | 0.29 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.45 | 51300 | 0.5 | 31.4 | stop | 5.06 | 4.07 | stop | 4.35 | stop | 6.44 | 0.05 | 1.29 | 6.25 | 53200 | 8300 | 1 | 0.05 | 0 | 0.48 | 5.34 | 1186 | 10 | 0.022 | 350.98 | 0.33 | 5.33 | 1425 | 14 | 0.022 | 434.54 | 0.37 | stop | stop | stop | stop | stop | stop | 6.7 | 777.3 | 0.32 | 0.63 | 6.62 | 1251 | 0.24 | 0.53 | 6.69 | 1292 | 0.04 | 0.68
2026-09-13
2026-09-14 | 12.9 | 104 | 7.53 | 53300 | 0.38 | 19.9 | 3.5 | 3.54 | 3.62 | 0.09 | 0.55 | 6.04 | 54600 | 6820 | 2 | 0.04 | 0 | 0.46 | 5.29 | 581 | 8 | 0.028 | 163.36 | 0.44 | 5.3 | 663.3 | 6 | 0.026 | 194.15 | 0.43 | 7.61 | 53500 | 0.33 | 40.1 | 4.96 | 4.44 | 4.46 | 6.32 | 0.09 | 0.75 | 6.28 | 53900 | 7720 | 2 | 0.05 | 0 | 0.49 | stop | stop | stop | stop | stop | stop | 5.3 | 557.9 | 4 | 0.018 | 163.77 | 0.48 | 7.63 | 53400 | 0.41 | 47.6 | 3.14 | 2.99 | 3.22 | 5.27 | 0.1 | 0.58 | 6.36 | 54200 | 8960 | 2 | 0.05 | 0 | 0.45 | 5.65 | 747 | 4 | 0.01 | 221.08 | 0.43 | 5.73 | 761.2 | 4 | 0.017 | 227.33 | 0.44 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.78 | 52800 | 0.46 | 20.7 | stop | stop | 5.16 | stop | 5.64 | stop | 7.65 | 0.04 | 0.89 | 6.25 | 53800 | 7120 | 1 | 0.05 | 0 | 0.5 | 5.38 | 1190 | 8 | 0.051 | 357.11 | 0.48 | 5.41 | 1382 | 10 | 0.051 | 457.69 | 0.46 | stop | stop | stop | stop | stop | stop | 6.79 | 630 | 0.02 | 0.58 | 6.64 | 747 | 0.04 | 0.56 | 6.62 | 1273 | 0.06 | 0.8
2026-09-15 | 13.6 | 33.7 | 7.86 | 64900 | 0.25 | 20.8 | 3.82 | 3.88 | 3.92 | 0.09 | 0.62 | 6.16 | 67100 | 7000 | 1 | 0.02 | 0 | 0.48 | 5.44 | 702.7 | 8 | 0.012 | 165.35 | 0.46 | 5.41 | 786 | 6 | 0.01 | 195.85 | 0.45 | 7.86 | 64900 | 0.36 | 46.7 | 5.85 | 4.98 | 5.35 | 7.63 | 0.07 | 0.86 | 6.29 | 66500 | 8480 | 2 | 0.05 | 0 | 0.5 | stop | stop | stop | stop | stop | stop | 5.45 | 680.96 | 6 | 0.015 | 152.73 | 0.48 | 7.86 | 65100 | 0.3 | 49.7 | 3.12 | 2.98 | 3.09 | 5.38 | 0.13 | 0.61 | 6.45 | 66800 | 6800 | 1 | 0.05 | 0 | 0.47 | 5.75 | 923.6 | 4 | 0.014 | 210.51 | 0.45 | 5.84 | 923.4 | 4 | 0.01 | 222.25 | 0.46 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.68 | 65000 | 0.24 | 20.1 | stop | 5.29 | 5.35 | stop | 4.9 | stop | 7.21 | 0.01 | 0.83 | 6.5 | 66500 | 7400 | 1 | 0.05 | 0 | 0.5 | 5.75 | 1426 | 8 | 0.014 | 345.32 | 0.49 | 5.7 | 1690 | 8 | 0.01 | 451.57 | 0.8 | 5.75 | 1683 | 10 | 0.01 | 411.54 | 0.5 | 7.31 | 754.5 | 0.01 | 0.36 | 7.37 | 1418 | 0.05 | 0.48 | 7.21 | 1592 | 0.17 | 0.76
2026-09-16 | 11.7 | 39.6 | 7.01 | 64500 | 0.2 | 18.3 | 4.12 | 4.24 | 4.34 | 0.1 | 0.67 | 6.02 | 65550 | 9720 | 1 | 0.04 | 0 | 0.5 | 5.34 | 703.8 | 8 | 0.025 | 175.62 | 0.48 | 5.37 | 774.5 | 8 | 0.013 | 193.98 | 0.77 | 6.94 | 65200 | 0.24 | 24.5 | 5.28 | 5.39 | 5.47 | 7.35 | 0.08 | 0.89 | 6.5 | 65100 | 7720 | 1 | 0.09 | 0 | 0.5 | 5.7 | 791.8 | 8 | 0.017 | 202.61 | 0.48 | 5.49 | 460.3 | 6 | 0.011 | 153.99 | 0.47 | 6.94 | 65200 | 0.23 | 31.2 | 3.23 | 2.9 | 3.16 | 5.42 | 0.08 | 0.67 | 6.47 | 65400 | 9080 | 1 | 0.05 | 0 | 0.48 | stop | stop | stop | stop | stop | stop | 5.48 | 991.1 | 4 | 0.014 | 258.86 | 0.46 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.94 | 64700 | 0.3 | 34.7 | stop | stop | 4.63 | stop | 4.93 | 4.81 | 5.72 | 0.02 | 0.75 | 6.26 | 65400 | 7120 | 1 | 0.04 | 0 | 0.5 | 5.53 | 1388 | 8 | 0.011 | 398.56 | 0.49 | 5.61 | 1656 | 10 | 0.018 | 454.98 | 0.48 | 5.67 | 1675 | 10 | 0.018 | 488.36 | 0.49 | 6.73 | 755.6 | 0.01 | 0.46 | 6.94 | 1022 | 0.1 | 0.48 | 6.5 | 1603 | 0.17 | 1.26
2026-09-17 | 9.75 | 11.2 | 7.41 | 64000 | 0.38 | 19.9 | 3.56 | 3.64 | 3.76 | 0.12 | 0.58 | 6.12 | 65500 | 5800 | 1 | 0.04 | 0 | 0.46 | 5.58 | 770.1 | 8 | 0.017 | 175.08 | 0.45 | 5.54 | 526.3 | 6 | 0.012 | 208.5 | 0.44 | 7.44 | 64100 | 0.47 | 36.4 | 4.67 | 4.52 | 4.88 | 6.13 | 0.18 | 0.75 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.41 | 63900 | 0.03 | 39.7 | 3.95 | 2.8 | 3.07 | 5.61 | 0.12 | 0.66 | 6.34 | 65300 | 6200 | 1 | 0.01 | 0 | 0.46 | 5.68 | 972.5 | 6 | 0.015 | 233.6 | 0.45 | 5.89 | 970.1 | 4 | 0.013 | 234.15 | 0.44 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.81 | 63600 | 0.29 | 20.4 | stop | stop | 3.92 | stop | 4.13 | stop | 5.78 | 0.01 | 0.77 | 6.29 | 65500 | 8200 | 1 | 0.04 | 0 | 0.5 | 5.96 | 1434 | 8 | 0.018 | 363.63 | 0.5 | 5.87 | 1744 | 8 | 0.014 | 459.89 | 0.48 | 5.82 | 1698 | 8 | 0.012 | 2588.54 | 0.49 | 6.84 | 699.6 | 0.01 | 0.45 | 6.76 | 1483 | 0.05 | 0.73 | 6.74 | 1744 | 0.62 | 1.16
2026-09-18 | 8.05 | 13.3 | 7.61 | 60100 | 0.31 | 18.5 | 3.43 | 3.54 | 3.63 | 0.04 | 0.57 | 6.19 | 62500 | 9720 | 1 | 0.02 | 0 | 0.44 | 5.46 | 720.9 | 8 | 0.01 | 182.51 | 0.41 | 5.4 | 769.7 | 8 | 0.01 | 180.11 | 0.4 | 7.63 | 60500 | 0.32 | 32.5 | 4.25 | 4.19 | 4.22 | 5.3 | 0.14 | 0.7 | 6.39 | 62300 | 7000 | 2 | 0.04 | 0 | 0.49 | stop | stop | stop | stop | stop | stop | 5.45 | 676.8 | 8 | 0.016 | 163.2 | 0.47 | 7.63 | 60200 | 0.28 | 37.4 | 2.8 | 2.77 | 2.85 | 4.65 | 0.21 | 0.61 | 7.07 | 62600 | 6400 | 1 | 0.03 | 0 | 0.45 | 5.7 | 932.7 | 6 | 0.01 | 237.6 | 0.43 | 5.76 | 932.6 | 6 | 0.01 | 236.4 | 0.42 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7 | 59200 | 0.26 | 18.4 | stop | 3.78 | 3.88 | stop | 3.9 | stop | 5.61 | 0.01 | 0.72 | 6.36 | 62400 | 8200 | 1 | 0.05 | 0 | 0.49 | stop | stop | stop | stop | stop | stop | 5.52 | 1645 | 8 | 0.026 | 423.53 | 0.46 | 5.6 | 1620 | 8 | 0.02 | 405.14 | 0.47 | 6.5 | 774 | 0.02 | 0.69 | 6.61 | 1204 | 0.03 | 0.82 | 6.57 | 1611 | 0.23 | 2.7
2026-09-19 | 15.8 | 16.6 | 7.48 | 58800 | 1.8 | 19.5 | 3.59 | 3.65 | 3.72 | 0.09 | 0.55 | 6.11 | 60200 | 8720 | 2 | 0.02 | 0 | 0.45 | 5.86 | 746.9 | 8 | 0.039 | 227.24 | 0.43 | 5.77 | 795 | 8 | 0.028 | 197.92 | 0.42 | 7.67 | 59200 | 1.59 | 37.1 | 5.16 | 4.84 | 4.97 | 6.34 | 0.08 | 0.87 | 6.31 | 60600 | 6480 | 2 | 0.05 | 0 | 0.5 | 5.78 | 770.6 | 8 | 0.035 | 186.42 | 0.48 | 5.82 | 654.8 | 8 | 0.034 | 157.7 | 0.48 | 7.79 | 59300 | 1.87 | 39.8 | 2.98 | 2.81 | 3.1 | 4.85 | 0.1 | 0.71 | 6.7 | 60500 | 6680 | 2 | 0.05 | 0 | 0.48 | stop | stop | stop | stop | stop | stop | 5.72 | 1000 | 6 | 0.029 | 258.15 | 0.46 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.53 | 58700 | 0.31 | 21.2 | stop | 3.81 | 3.78 | stop | 3.92 | stop | 5.82 | 0.02 | 0.78 | 6.46 | 60300 | 7400 | 2 | 0.05 | 0 | 0.5 | 5.68 | 1580 | 10 | 0.038 | 431.86 | 0.48 | 5.66 | 1603 | 10 | 0.045 | 433.6 | 0.47 | 5.68 | 1606 | 10 | 0.043 | 462.02 | 0.49 | 7.2 | 790.8 | 0.02 | 0.98 | 7.14 | 869.4 | 0.08 | 0.41 | 7.11 | 1515 | 0.16 | 1.26
2026-09-20
2026-09-21 | 8.51 | 9.09 | 7.08 | 58500 | 0.46 | 18.9 | 3.64 | 3.76 | 3.96 | 0.03 | 0.89 | 6.23 | 59000 | 8440 | 2 | 0.02 | 0 | 0.48 | 5.67 | 681.6 | 4 | 0.028 | 175.49 | 0.42 | 5.7 | 710.1 | 2 | 0.014 | 186.74 | 0.47 | 7.21 | 58900 | 0.5 | 37.6 | 5.42 | 5.01 | 5.52 | 6.2 | 0.05 | 0.94 | 6.28 | 60100 | 8040 | 2 | 0.02 | 0 | 0.42 | 5.82 | 723.6 | 4 | 0.01 | 187.76 | 0.4 | 5.86 | 603.2 | 2 | 0.008 | 156.52 | 0.33 | 7.3 | 59000 | 0.5 | 40.1 | 3.38 | 3.57 | 3.05 | 5.06 | 0.04 | 0.92 | 6.26 | 60200 | 8920 | 3 | 0.03 | 0 | 0.5 | stop | stop | stop | stop | stop | stop | 5.73 | 945.1 | 2 | 0.003 | 254.93 | 0.35 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.6 | 58800 | 0.2 | 33.4 | stop | 4.97 | 3.35 | stop | 3.21 | stop | 4.55 | 0.17 | 0.63 | 6.42 | 59600 | 7000 | 2 | 0.04 | 0 | 0.46 | 5.62 | 1272 | 10 | 0.015 | 364.58 | 0.46 | 5.66 | 1522 | 14 | 0.011 | 455.76 | 0.34 | 5.73 | 1575 | 18 | 0.025 | 456.52 | 0.27 | 6.87 | 743.5 | 0.02 | 0.63 | 6.65 | 1168 | 0.05 | 0.4 | 6.5 | 1418 | 0.07 | 0.57
2026-09-22 | 6.69 | 7.45 | 7.49 | 58600 | 0.24 | 20.6 | 3.78 | 4.01 | 3.98 | 0.08 | 0.7 | 6.14 | 60900 | 7480 | 2 | 0.03 | 0 | 0.45 | 5.78 | 718.9 | 1 | 0.029 | 189.03 | 0.44 | 5.75 | 702.8 | 4 | 0.012 | 183.84 | 0.49 | 7.46 | 59600 | 0.25 | 48.2 | 5.41 | 4.84 | 5.3 | 6.24 | 0.09 | 0.78 | 6.19 | 62100 | 7320 | 1 | 0.03 | 0 | 0.44 | 5.8 | 722.7 | 4 | 0.018 | 188.51 | 0.42 | 5.75 | 619.1 | 2 | 0.01 | 157.85 | 0.42 | 7.67 | 59700 | 0.24 | 50.7 | 3 | 2.99 | 2.81 | 5.51 | 0.08 | 0.89 | 6.19 | 62300 | 9120 | 2 | 0.02 | 0 | 0.46 | stop | stop | stop | stop | stop | stop | 5.63 | 1000 | 4 | 0.005 | 258.42 | 0.37 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.93 | 59200 | 0.2 | 31.5 | stop | 4.2 | stop | stop | 3.55 | 3.32 | 5.14 | 0.07 | 0.82 | 6.28 | 61300 | 7520 | 1 | 0.04 | 0 | 0.46 | 5.57 | 1270 | 10 | 0.028 | 356.48 | 0.46 | 5.54 | 1551 | 14 | 0.034 | 433.86 | 0.33 | 5.6 | 1599 | 16 | 0.0025 | 450.1 | 0.4 | 6.95 | 756.3 | 0.07 | 0.42 | 6.68 | 1363 | 0.07 | 0.28 | 6.66 | 1487 | 0.06 | 0.44
2026-09-23 | 9.35 | 11.6 | 7.02 | 59900 | 0.35 | 18.4 | 3.33 | 3.67 | 3.86 | 0.14 | 0.69 | 6.08 | 61300 | 7000 | 1 | 0.02 | 0 | 0.45 | 5.59 | 728.7 | 12 | 0.03 | 183.19 | 0.43 | 5.66 | 729.7 | 2 | 0.036 | 187.98 | 0.44 | 7.06 | 60500 | 0.25 | 43.7 | 6.37 | 4.3 | 4.57 | 6.07 | 0.17 | 0.65 | 6.1 | 62700 | 7320 | 2 | 0.03 | 0 | 0.45 | 5.69 | 768.8 | 4 | 0.035 | 195.86 | 0.43 | 5.7 | 637.5 | 2 | 0.023 | 159.61 | 0.37 | 7.09 | 60200 | 0.26 | 40.1 | 2.88 | 2.95 | 3.16 | 5.06 | 0.09 | 0.83 | 6.14 | 62500 | 7280 | 2 | 0.03 | 0 | 0.48 | stop | stop | stop | stop | stop | stop | 5.6 | 961.8 | 4 | 0.026 | 244.71 | 0.4 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.13 | 59900 | 0.22 | 38.1 | stop | 3.46 | stop | 4.09 | 3.49 | stop | 5.06 | 0.06 | 0.68 | 6.22 | 61500 | 8720 | 1 | 0.07 | 0 | 0.5 | 5.58 | 1335 | 8 | 0.024 | 34.62 | 0.24 | 5.6 | 1685 | 14 | 0.032 | 432.16 | 0.42 | 5.74 | 1767 | 16 | 0.033 | 470.32 | 0.39 | 6.58 | 771.6 | 0.01 | 0.73 | 6.56 | 1503 | 0.1 | 0.41 | 6.58 | 1501 | 0.08 | 0.32
2026-09-24 | 8.65 | 9.24 | 7.41 | 58600 | 0.4 | 24.6 | 3.33 | 3.42 | 3.85 | 0.08 | 0.87 | 6.5 | 59900 | 7480 | 2 | 0.02 | 0 | 0.5 | 5.66 | 722.6 | 10 | 0.03 | 208.65 | 0.44 | 5.68 | 692.3 | 4 | 0.025 | 195.32 | 0.43 | 7.49 | 59100 | 0.33 | 47.5 | 5.48 | 4.31 | 5.2 | 6.28 | 0.07 | 0.78 | 6.46 | 61300 | 7600 | 1 | 0.02 | 0 | 0.47 | 5.78 | 792.8 | 4 | 0.026 | 202.51 | 0.46 | 5.67 | 605 | 4 | 0.027 | 164.96 | 0.44 | 7.46 | 59000 | 0.21 | 49.7 | 2.67 | 3.21 | 3.07 | 5.66 | 0.09 | 0.51 | 6.35 | 61400 | 7600 | 1 | 0.01 | 0.02 | 0.49 | stop | stop | stop | stop | stop | stop | 5.62 | 876.6 | 4 | 0.025 | 252.49 | 0.45 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.37 | 58500 | 0.29 | 40.1 | stop | 3.67 | stop | 3.88 | 3.9 | stop | 5.22 | 0.09 | 0.97 | 6.4 | 60200 | 7400 | 1 | 0.05 | 0.01 | 0.43 | 5.59 | 1253 | 10 | 0.025 | 353.05 | 0.4 | 5.58 | 1536 | 14 | 0.043 | 483.5 | 0.41 | 5.64 | 1538 | 14 | 0.051 | 361.85 | 0.42 | 6.6 | 745 | 0.04 | 0.84 | 6.5 | 1353 | 0.1 | 0.5 | 6.92 | 1521 | 0.15 | 0.25
2026-09-25 | 28.4 | 12.5 | 7.1 | 58900 | 0.2 | 20.3 | 3.34 | 3.83 | 3.9 | 0.19 | 0.97 | 6.18 | 61000 | 7880 | 1 | 0.04 | 0 | 0.43 | 5.77 | 721.8 | 16 | 0.033 | 197.28 | 0.19 | 5.8 | 651.1 | 2 | 0.028 | 180.84 | 0.17 | 7.16 | 59100 | 0.21 | 37.2 | 5.59 | 4.92 | 5.1 | 6.2 | 0.3 | 0.65 | 6.16 | 62400 | 7560 | 2 | 0.02 | 0 | 0.4 | stop | stop | stop | stop | stop | stop | 5.79 | 618.4 | 4 | 0.016 | 179.09 | 0.18 | 7.16 | 58700 | 0.23 | 34.5 | 3.22 | 3.32 | 3.26 | 5.51 | 0.13 | 0.76 | 6.16 | 62400 | 7480 | 1 | 0.04 | 0 | 0.45 | stop | stop | stop | stop | stop | stop | 5.69 | 907.6 | 2 | 0.055 | 258.15 | 0.36 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.1 | 58000 | 0.2 | 36.3 | stop | 3.69 | stop | stop | 3.73 | stop | 5.6 | 0.18 | 0.79 | 6.22 | 61500 | 7400 | 2 | 0.05 | 0 | 0.47 | 5.47 | 1297 | 8 | 0.062 | 387.34 | 0.21 | 5.44 | 1597 | 14 | 0.054 | 479.9 | 0.22 | stop | stop | stop | stop | stop | stop | 6.98 | 719.4 | 0.07 | 0.59 | 7.94 | 781.1 | 0.06 | 0.28 | 7.21 | 1637 | 0.14 | 0.63
2026-09-26 | 8.71 | 9.51 | 7.01 | 54300 | 0.22 | 22.7 | 3.9 | 3.8 | 3.98 | 0.06 | 0.8 | 6.11 | 53800 | 8080 | 1 | 0.03 | 0 | 0.45 | 5.93 | 670.6 | 16 | 0.1 | 184.67 | 0.45 | 6.05 | 637.3 | 6 | 0.01 | 181.36 | 0.44 | 7.11 | 54500 | 0.21 | 56.5 | 4.87 | 4.89 | 5.2 | 6.21 | 0.06 | 0.82 | 6.69 | 54900 | 8680 | 2 | 0.01 | 0 | 0.45 | stop | stop | stop | stop | stop | stop | 5.9 | 650.8 | 2 | 0.06 | 183.15 | 0.29 | 7.17 | 54300 | 0.24 | 47.1 | 2.77 | 2.86 | 2.76 | 5.4 | 0.32 | 0.74 | 6.45 | 54800 | 7600 | 2 | 0.02 | 0 | 0.49 | stop | stop | stop | stop | stop | stop | 5.88 | 907.6 | 4 | 0.011 | 258.12 | 0.42 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.07 | 51900 | 0.26 | 52.4 | stop | 3.33 | stop | stop | 3.6 | stop | 4.3 | 0.02 | 0.94 | 6.48 | 53700 | 7920 | 1 | 0.04 | 0 | 0.47 | 5.71 | 1312 | 8 | 0.012 | 402.3 | 0.44 | stop | stop | stop | stop | stop | stop | 5.69 | 1239 | 16 | 0.036 | 378.5 | 0.41 | 6.85 | 714.5 | 0.06 | 0.98 | 6.92 | 909.8 | 0.1 | 0.77 | 6.83 | 1455 | 0.11 | 0.86
2026-09-27
2026-09-28 | 53.8 | 90.8 | 7.6 | 57600 | 0.26 | 21.8 | 3.3 | 3.5 | 4.18 | 0.24 | 0.58 | 6.73 | 61200 | 8800 | 2 | 0.02 | 0 | 0.35 | 5.54 | 776.6 | 10 | 0.049 | 227.5 | 0.26 | 5.45 | 673.8 | 4 | 0.044 | 196.45 | 0.48 | 7.14 | 59100 | 0.24 | 32.4 | 5.22 | 5.95 | 5.57 | 6.98 | 0.03 | 0.9 | 6.88 | 60500 | 7680 | 2 | 0.05 | 0 | 0.5 | 5.89 | 789.2 | 8 | 0.042 | 236.05 | 0.27 | 5.6 | 660.9 | 6 | 0.044 | 193.4 | 0.31 | 7.76 | 57800 | 0.47 | 39.2 | 3.91 | 3.19 | 3.85 | 5.98 | 0.07 | 0.85 | 6.86 | 60400 | 8440 | 2 | 0.05 | 0 | 0.5 | stop | stop | stop | stop | stop | stop | 5.93 | 908 | 6 | 0.12 | 260.1 | 0.3 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.07 | 59800 | 0.28 | 38.5 | stop | 4.84 | stop | 0.77 | 5.44 | 4.92 | 6.98 | 0.03 | 0.55 | 6.66 | 60700 | 7480 | 2 | 0.05 | 0 | 0.5 | 5.74 | 1151 | 16 | 0.082 | 235.74 | 0.29 | 5.71 | 1350 | 18 | 0.062 | 423.8 | 0.26 | 5.63 | 1320 | 16 | 0.07 | 401.12 | 0.3 | 7.15 | 814.8 | 0.06 | 0.84 | 7.04 | 1233 | 0.08 | 0.6 | 6.83 | 1271 | 0.11 | 0.48
2026-09-29 | 20 | 127 | 7.45 | 58700 | 0.22 | 22.3 | 3.94 | 3.85 | 4.8 | 0.03 | 0.8 | 6.42 | 61200 | 9820 | 2 | 0.02 | 0 | 0.38 | 5.85 | 870.1 | 12 | 0.095 | 242.01 | 0.26 | stop | stop | stop | stop | stop | stop | 7.6 | 58800 | 0.21 | 31.6 | 6.49 | 5.35 | 5.46 | 6.9 | 0.13 | 0.88 | 6.5 | 61200 | 9360 | 2 | 0.03 | 0 | 0.5 | 5.93 | 893.6 | 6 | 0.046 | 244.79 | 0.22 | 5.8 | 749.8 | 6 | 0.082 | 206.69 | 0.2 | 7.64 | 58400 | 0.21 | 37.4 | 4.62 | 4.32 | 3.89 | 5.96 | 0.21 | 0.9 | 6.49 | 60600 | 8880 | 2 | 0.03 | 0 | 0.49 | stop | stop | stop | stop | stop | stop | 5.96 | 1029 | 6 | 0.026 | 290.59 | 0.21 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.6 | 58000 | 0.25 | 36.2 | stop | 4.31 | stop | stop | 4.64 | 5.67 | 6.9 | 0.01 | 0.8 | 6.47 | 60400 | 9480 | 2 | 0.03 | 0 | 0.49 | 5.6 | 1291 | 14 | 0.022 | 365.62 | 0.18 | 5.58 | 1541 | 14 | 0.026 | 465.68 | 0.35 | 5.89 | 1536 | 26 | 0.036 | 480.72 | 0.24 | 7.12 | 864 | 0.08 | 0.71 | 7.32 | 1403 | 0.16 | 0.98 | 7 | 1452 | 0.07 | 0.76
2026-09-30 | 31.7 | 91.8 | stop | stop | stop | stop | 3.73 | 3.85 | 4.15 | 0.29 | 0.4 | 6.4 | 61300 | 9004 | 2 | 0.04 | 0 | 0.3 | 5.84 | 942.4 | 14.8 | 0.073 | 252.55 | 0.25 | stop | stop | stop | stop | stop | stop | 6.67 | 60100 | 0.47 | 30.4 | 5.97 | 6.22 | 6.08 | 6.97 | 0.11 | 0.83 | 6.5 | 61200 | 11340 | 2 | 0.05 | 0 | 0.5 | 5.94 | 912.8 | 7.2 | 0.045 | 250.48 | 0.29 | 5.87 | 756.7 | 6 | 0.044 | 208.3 | 0.29 | 6.71 | 60600 | 0.49 | 45.6 | 3.73 | 3.85 | 3.73 | 5.94 | 0.22 | 0.89 | 6.49 | 61500 | 10100 | 1 | 0.05 | 0 | 0.5 | stop | stop | stop | stop | stop | stop | 5.86 | 1042 | 7.8 | 0.034 | 295.01 | 0.28 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.22 | 60600 | 0.29 | 34.9 | stop | 4.12 | stop | stop | 3.48 | 5.29 | 6.73 | 0.02 | 0.6 | 6.45 | 60900 | 10968 | 2 | 0.05 | 0 | 0.5 | 5.65 | 1427 | 20.6 | 0.056 | 425.4 | 0.22 | 5.67 | 1649 | 18 | 0.051 | 482.76 | 0.24 | 5.69 | 1614 | 20 | 0.06 | 492.74 | 0.21 | 6.8 | 1117 | 0.18 | 1.07 | 7.05 | 1614 | 0.09 | 0.62 | 6.63 | 1586 | 0.01 | 0.7
2026-10-01
INTAKE SWRO |  |  | SWRO #1 | [27 empty] | SWRO #2 | [28 empty] | SWRO #3 | [28 empty] | SWRO #4 | [12 empty] | SWRO #3 | [37 empty] | PRODUCT SWRO
| INTAKE 1 | INTAKE 2 | INLET DAF |  |  |  | OUTLET DAF |  | INLET MMF | OUTLET MMF |  | FEED WATER | [6 empty] | PERMEATE R/O #1A | [5 empty] | PERMEATE R/O #1B | [5 empty] | INLET DAF |  |  |  | OUTLET DAF |  |  | INLET MMF | OUTLET MMF |  | FEED WATER | [6 empty] | PERMEATE R/O #2A | [5 empty] | PERMEATE R/O #2B | [5 empty] | INLET DAF |  |  |  | OUTLET DAF |  |  | INLET MMF | OUTLET MMF |  | FEED WATER | [6 empty] | PERMEATE R/O #3A | [5 empty] | PERMEATE R/O #3B | [5 empty] | FEED WATER | [6 empty] | PERMEATE R/O #4 | [5 empty] | INLET DAF |  |  |  | OUTLET DAF |  |  | OUTLET DAF |  |  | INLET MMF | OUTLET MMF |  | FEED WATER | [6 empty] | PERMEATE R/O #5A | [5 empty] | PERMEATE R/O #5B | [5 empty] | PERMEATE R/O #5C | [5 empty] | PERMEATE SWRO #1 |  |  |  | PERMEATE SWRO #2,#3,#4 |  |  |  | PERMEATE SWRO #5
Parameter | Turbidity | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | Turbidity DAF 1 | Turbidity DAF 2 | Turbidity | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | Turbidity DAF 1 | Turbidity DAF 2 | Turbidity DAF 3 | Turbidity | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | Turbidity DAF 1 | Turbidity DAF 2 | Turbidity DAF 3 | Turbidity | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | Turbidity | pH | Conductivity | Free Chlorine | Turbidity | Turbidity DAF 1 | Turbidity DAF 2 | Turbidity DAF 3 | Turbidity DAF 1 | Turbidity DAF 2 | Turbidity DAF 3 | Turbidity | Iron | Turbidity | pH | Conductivity | T. Hardness | Silica | Iron | Free Chlorine | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | Turbidity | pH | Conductivity | T. Hardness | Silica | Chloride | Turbidity | pH | Conductivity | Iron | Turbidity | pH | Conductivity | Iron | Turbidity | pH | Conductivity | Iron | Turbidity
| NTU | NTU |  | (µS/cm) | (ppm Cl2) | NTU | NTU | NTU | NTU | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) | NTU |  | (µS/cm) | (ppm Cl2) | NTU | NTU | NTU | NTU | NTU | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) | NTU |  | (µS/cm) | (ppm Cl2) | NTU | NTU | NTU | NTU | NTU | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) | NTU |  | (µS/cm) | (ppm Cl2) | NTU | NTU | NTU | NTU | NTU | NTU | NTU | NTU | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | (ppm Cl2) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppmCl-) | NTU |  | (µS/cm) | (ppm Fe) | NTU |  | (µS/cm) | (ppm Fe) | NTU |  | (µS/cm) | (ppm Fe) | NTU
| N/A | N/A | N/A | N/A | 0.2 - 0.5 | N/A | < 5 | < 5 | < 5 | N/A | < 1 | 6.0 - 6.5 | N/A | N/A | N/A | max 0.05 | < 0.05 | < 0.5 | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | N/A | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | N/A | N/A | N/A | 0.2 - 0.5 | N/A | < 5 | < 5 | < 5 | < 5 | N/A | < 1 | 6.0 - 6.5 | N/A | N/A | N/A | max 0.05 | < 0.05 | < 0.5 | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | N/A | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | N/A | N/A | N/A | 0.2 - 0.5 | N/A | < 5 | < 5 | < 5 | < 5 | N/A | < 1 | 6.0 - 6.5 | N/A | N/A | N/A | max 0.05 | < 0.05 | < 0.5 | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | < 0.5 | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | < 0.5 | 6.0 - 6.5 | N/A | N/A | N/A | max 0.05 | < 0.05 | < 0.5 | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | N/A | N/A | N/A | 0.2 - 0.5 | N/A | < 5 | < 5 | < 5 | < 5 | < 5 | < 5 | < 5 | N/A | < 1 | 6.0 - 6.5 | N/A | N/A | N/A | max 0.05 | < 0.05 | < 0.5 | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | N/A | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | N/A | 5.0 - 7.0 | < 1000 | N/A | N/A | N/A | N/A | 6.5 - 7.5 | < 1000 | N/A | N/A | 6.5 - 7.5 | < 1000 | N/A | N/A | 6.5 - 7.5 | < 1000 | N/A | N/A
2026-09-01 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | stop | stop | 0% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 0% | 0% | 0% | stop | 0% | stop | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-02 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | 100% | stop | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-03 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | stop | 100% | stop | 100% | stop | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-04 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | stop | 100% | stop | 100% | stop | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-05 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | stop | 100% | stop | 100% | stop | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-06 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-07 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 0% | 100% | stop | 100% | stop | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-08 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-09 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-10 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-11 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | 100% | 100% | stop | 0% | stop | 0% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-12 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | 0% | 100% | stop | 100% | stop | 0% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-13 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-14 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | 0% | stop | 0% | stop | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-15 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | 0% | 0% | stop | 100% | stop | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-16 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | 100% | stop | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-17 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | 100% | stop | 100% | stop | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-18 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | 100% | 100% | stop | 100% | stop | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-19 | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 0% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | 100% | 100% | stop | 100% | stop | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | no data | no data | no data | no data | 100% | no data | no data | 100% | 100% | no data | no data | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-20 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-21 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | 100% | 100% | stop | 100% | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-22 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | 100% | stop | stop | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-23 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | 100% | stop | 100% | 100% | stop | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-24 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | no data | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | 100% | stop | 100% | 100% | stop | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-25 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | 100% | stop | stop | 100% | stop | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-26 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | 100% | stop | stop | 100% | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-27 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-28 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | 100% | stop | 100% | 0% | 100% | 0% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-29 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 0% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | 100% | stop | stop | 100% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100%
2026-09-30 | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | 100% | 0% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | 100% | stop | stop | 100% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | 100%
2026-10-01 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
CONFORMANCE | 100% | 100% | 100% | 100% | 96% | 100% | 100% | 100% | 100% | 100% | 100% | 96.15% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 96.15% | 100% | 15.38% | 41.67% | 24% | 0% | 100% | 100% | 91.67% | 100% | 100% | 100% | 95.83% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 92.31% | 100% | 100% | 100% | 100% | 7.692% | 100% | 100% | 88.46% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 92.31% | 100% | 100% | 100% | 100% | [13 empty] | 100% | 100% | 100% | 100% | 83.33% | 76.47% | 80% | 100% | 82.61% | 60% | 8.696% | 100% | 91.3% | 96.15% | 100% | 100% | 100% | 88.46% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 96% | 100% | 100% | 96% | 24% | 100% | 100% | 100% | 0% | 100% | 100%
OVERALL VALUE
Date | SWRO #1 | SWRO #2 | SWRO #3 | SWRO #4 | PRODUCT SWRO
2026-09-01 | 100% | 75% | 95.65% | stop | 83.33%
2026-09-02 | 100% | 75% | 96.55% | stop | 80%
2026-09-03 | 100% | 82.61% | 96.55% | stop | 90%
2026-09-04 | 100% | 82.61% | 96.55% | stop | 80%
2026-09-05 | 100% | 93.1% | 96.55% | stop | 90%
2026-09-06 | no data | no data | no data | no data | no data
2026-09-07 | 100% | 86.21% | 95.65% | stop | 80%
2026-09-08 | 100% | 82.61% | 96.55% | stop | 80%
2026-09-09 | 100% | 82.61% | 96.55% | stop | 80%
2026-09-10 | 100% | 82.61% | 96.55% | stop | 80%
2026-09-11 | 100% | 82.61% | 96.55% | stop | 80%
2026-09-12 | 100% | 82.61% | 96.55% | stop | 80%
2026-09-13 | no data | no data | no data | no data | no data
2026-09-14 | 100% | 95.65% | 96.55% | stop | 90%
2026-09-15 | 100% | 86.96% | 96.55% | stop | 80%
2026-09-16 | 100% | 82.76% | 95.65% | stop | 80%
2026-09-17 | 100% | 90% | 93.1% | stop | 80%
2026-09-18 | 100% | 95.65% | 96.55% | stop | 90%
2026-09-19 | 96.43% | 89.66% | 91.3% | stop | 83.33%
2026-09-20 | no data | no data | no data | no data | no data
2026-09-21 | 100% | 86.21% | 95.65% | stop | 80%
2026-09-22 | 100% | 89.66% | 95.65% | stop | 80%
2026-09-23 | 100% | 93.1% | 95.65% | stop | 80%
2026-09-24 | 100% | 89.29% | 95.65% | stop | 80%
2026-09-25 | 100% | 86.96% | 95.65% | stop | 80%
2026-09-26 | 100% | 86.96% | 95.65% | stop | 90%
2026-09-27 | no data | no data | no data | no data | no data
2026-09-28 | 96.43% | 82.76% | 91.3% | stop | 80%
2026-09-29 | 100% | 86.21% | 91.3% | stop | 80%
2026-09-30 | stop | 86.21% | 91.3% | stop | 70%
2026-10-01 | no data | no data | no data | no data | no data
CONFORMANCE | 99.71% | 85.98% | 95.3% |  | 81.79%
SWRO
2026-09-01 | 88.5%
2026-09-02 | 87.89%
2026-09-03 | 92.29%
2026-09-04 | 89.79%
2026-09-05 | 94.91%
2026-09-06
2026-09-07 | 90.46%
2026-09-08 | 89.79%
2026-09-09 | 89.79%
2026-09-10 | 89.79%
2026-09-11 | 89.79%
2026-09-12 | 89.79%
2026-09-13
2026-09-14 | 95.55%
2026-09-15 | 90.88%
2026-09-16 | 89.6%
2026-09-17 | 90.78%
2026-09-18 | 95.55%
2026-09-19 | 90.18%
2026-09-20
2026-09-21 | 90.46%
2026-09-22 | 91.33%
2026-09-23 | 92.19%
2026-09-24 | 91.23%
2026-09-25 | 90.65%
2026-09-26 | 93.15%
2026-09-27
2026-09-28 | 87.62%
2026-09-29 | 89.38%
2026-09-30 | 82.5%
2026-10-01

## BOILER&BFW
| DEMIN TANK 2000 MT | [5 empty] | CONDENSATE TANK 200 MT |  |  |  |  | BFW PP#1 | [6 empty] | BFW PP#2 | [6 empty] | BFW PP#3 | [6 empty] | BFW CFBC | [6 empty] | BFW HP Coal | [6 empty] | BFW HP Gas | [6 empty] | BFW MP | [5 empty] | BFW TOH #3/#4 | [5 empty] | BFW HRSG GT #1 | [5 empty] | BFW HRSG GT #2 | [5 empty] | BFW OMNICAL | [5 empty] | Boiler PP #1 |  |  |  | Boiler PP #2 |  |  |  | Boiler PP #3 |  |  |  | Boiler PP #4 |  |  |  | Boiler CFBC |  |  |  | Boiler HP Coal |  |  |  | Boiler HP Gas |  |  |  | Boiler MP | [7 empty] | Boiler HRSG TOH #3 | [7 empty] | Boiler HRSG TOH #4 | [7 empty] | Boiler HRSG GT #1 | [7 empty] | Boiler HRSG GT #2 | [7 empty] | Boiler OMNICAL | [7 empty] | Condensate Turbin #3 |  |  | Condensate Header MPS - PP |  | Condensate Header LPS - PP |  | Condensate Header MPS - BH |  | Condensate Header HPS - BH |  | Condensate Header MPS - GT
Parameter | pH | Conductivity | T. Hardness | Silica | Iron | Turbidity | pH | Conductivity | T. Hardness | Iron | Turbidity | pH | Conductivity | Iron | T. Hardness | Turbidity | Surgard | DO | pH | Conductivity | Iron | T. Hardness | Turbidity | Surgard | DO | pH | Conductivity | Iron | T. Hardness | Turbidity | Surgard | DO | pH | Conductivity | Iron | T. Hardness | Turbidity | Surgard | DO | pH | Conductivity | Iron | T. Hardness | Turbidity | Surgard | DO | pH | Conductivity | Iron | T. Hardness | Turbidity | Surgard | DO | pH | Conductivity | Iron | T. Hardness | Turbidity | DO | pH | Conductivity | Iron | T. Hardness | Turbidity | DO | pH | Conductivity | Iron | T. Hardness | Turbidity | DO | pH | Conductivity | Iron | T. Hardness | Turbidity | DO | pH | Conductivity | Iron | T. Hardness | Turbidity | DO | pH | Conductivity | Silica | Phosphate | pH | Conductivity | Silica | Phosphate | pH | Conductivity | Silica | Phosphate | pH | Conductivity | Silica | Phosphate | pH | Conductivity | Silica | Phosphate | pH | Conductivity | Silica | Phosphate | pH | Conductivity | Silica | Phosphate | pH | Conductivity | P - Alkalinity | M - Alkalinity | O - Alkalinity | Silica | Phosphate | Sulphite | pH | Conductivity | P - Alkalinity | M - Alkalinity | O - Alkalinity | Silica | Phosphate | Sulphite | pH | Conductivity | P - Alkalinity | M - Alkalinity | O - Alkalinity | Silica | Phosphate | Sulphite | pH | Conductivity | P - Alkalinity | M - Alkalinity | O - Alkalinity | Silica | Phosphate | Sulphite | pH | Conductivity | P - Alkalinity | M - Alkalinity | O - Alkalinity | Silica | Phosphate | Sulphite | pH | Conductivity | P - Alkalinity | M - Alkalinity | O - Alkalinity | Silica | Phosphate | Sulphite | pH | Conductivity | Silica | pH | Conductivity | pH | Conductivity | pH | Conductivity | pH | Conductivity | pH | Conductivity
|  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) | NTU |  | (µS/cm) | (ppm CaCO3) | (ppm Fe) | (NTU) |  | (µS/cm) | (ppm Fe) | (ppm CaCO3) | NTU | (ppm surgard) | (ppb) |  | (µS/cm) | (ppm Fe) | (ppm CaCO3) | NTU | (ppm surgard) | (ppb) |  | (µS/cm) | (ppm Fe) | (ppm CaCO3) | NTU | (ppm surgard) | (ppb) |  | (µS/cm) | (ppm Fe) | (ppm CaCO3) | NTU | (ppm surgard) | (ppb) |  | (µS/cm) | (ppm Fe) | (ppm CaCO3) | NTU | (ppm surgard) | (ppb) |  | (µS/cm) | (ppm Fe) | (ppm CaCO3) | NTU | (ppm surgard) | (ppb) |  | (µS/cm) | (ppm Fe) | (ppm CaCO3) | NTU | (ppb) |  | (µS/cm) | (ppm Fe) | (ppm CaCO3) | NTU | (ppb) |  | (µS/cm) | (ppm Fe) | (ppm CaCO3) | NTU | (ppb) |  | (µS/cm) | (ppm Fe) | (ppm CaCO3) | NTU | (ppb) |  | (µS/cm) | (ppm Fe) | (ppm CaCO3) | NTU | (ppb) |  | (µS/cm) | (ppm SiO2) | ppm PO4 |  | (µS/cm) | (ppm SiO2) | ppm PO4 |  | (µS/cm) | (ppm SiO2) | ppm PO4 |  | (µS/cm) | (ppm SiO2) | ppm PO4 |  | (µS/cm) | (ppm SiO2) | ppm PO4 |  | (µS/cm) | (ppm SiO2) | ppm PO4 |  | (µS/cm) | (ppm SiO2) | ppm PO4 |  | (µS/cm) | (ppm) | (ppm) | (ppm) | (ppm SiO2) | ppm PO4 | (ppm sulphite) |  | (µS/cm) | (ppm) | (ppm) | (ppm) | (ppm SiO2) | ppm PO4 | (ppm sulphite) |  | (µS/cm) | (ppm) | (ppm) | (ppm) | (ppm SiO2) | ppm PO4 | (ppm sulphite) |  | (µS/cm) | (ppm) | (ppm) | (ppm) | (ppm SiO2) | ppm PO4 | (ppm sulphite) |  | (µS/cm) | (ppm) | (ppm) | (ppm) | (ppm SiO2) | ppm PO4 | (ppm sulphite) |  | (µS/cm) | (ppm) | (ppm) | (ppm) | (ppm SiO2) | ppm PO4 | (ppm sulphite) |  | (µS/cm) | (ppm SiO2) |  | (µS/cm) |  | (µS/cm) |  | (µS/cm) |  | (µS/cm) |  | (µS/cm)
| 5.5 - 7.0 | < 25.0 | 0.1; Max | 0.16 ; Max | 0.05 ; Max | <1 | 8.0 - 9.2 | 10.00; Max | 1.50 ; Max | 0.10 ; Max | 5 ; Max | 8.8 - 9.3 | 25 ; Max | 0.05 ; Max | 0.1; Max | N/A | 0.8-1.2 | 15 ; Max | 8.8 - 9.3 | 25 ; Max | 0.05 ; Max | 0.1; Max | N/A | 0.8-1.2 | 15 ; Max | 8.8 - 9.3 | 25 ; Max | 0.05 ; Max | 0.1; Max | N/A | 0.8-1.2 | 15 ; Max | 8.8 - 9.6 | 25 ; Max | 0.05 ; Max | 0.1; Max | N/A | 0.8-1.2 | 15 ; Max | 8.8 - 9.6 | 25 ; Max | 0.05 ; Max | 0.1; Max | 5 ; Max | 0.8-1.2 | 15 ; Max | 8.8 - 9.6 | 25 ; Max | 0.05 ; Max | 0.1; Max | 5 ; Max | 0.8-1.2 | 15 ; Max | 8.3 - 10.5 | 110 ; Max | 0.3 ; Max | 1.5; Max | 5 ; Max | 15 ; Max | 8.3 - 10.5 | 110 ; Max | 0.3 ; Max | 1.5; Max | 5 ; Max | 15 ; Max | 8.3 - 10.5 | 110 ; Max | 0.3 ; Max | 1.5; Max | 5 ; Max | 15 ; Max | 8.3 - 10.5 | 110 ; Max | 0.3 ; Max | 1.5; Max | 5 ; Max | 15 ; Max | 8.3 - 10.5 | 110 ; Max | 0.3 ; Max | 1.5; Max | 5 ; Max | 15 ; Max | 9.0 - 11.0 | 500 ; Max | 15 ; Max | 5.0 - 15.0 | 9.0 - 11.0 | 500 ; Max | 15 ; Max | 5.0 - 15.0 | 9.0 - 11.0 | 500 ; Max | 15 ; Max | 5.0 - 15.0 | 9.0 - 11.0 | 500 ; Max | 15 ; Max | 5.0 - 15.0 | 9.0 - 11.0 | 3200 ; Max | 8 ; Max | 5.0 - 15.0 | 9.0 - 11.0 | 3200 ; Max | 8 ; Max | 5.0 - 15.0 | 9.0 - 11.0 | 3200 ; Max | 8 ; Max | 5.0 - 15.0 | 10.0 - 12.0 | 4800 ; Max | 700 ; Max | 500 ; Max | 300 ; Max | 150; Max | 10 - 30 | 10 - 30 | 10.0 - 12.0 | 4800 ; Max | 700 ; Max | 500 ; Max | 300 ; Max | 150; Max | 10 - 30 | 10 - 30 | 10.0 - 12.0 | 4800 ; Max | 700 ; Max | 500 ; Max | 300 ; Max | 150; Max | 10 - 30 | 10 - 30 | 10.0 - 12.0 | 4800 ; Max | 700 ; Max | 500 ; Max | 300 ; Max | 150; Max | 10 - 30 | 10 - 30 | 10.0 - 12.0 | 4800 ; Max | 700 ; Max | 500 ; Max | 300 ; Max | 150; Max | 10 - 30 | 10 - 30 | 10.0 - 12.0 | 4800 ; Max | 700 ; Max | 500 ; Max | 300 ; Max | 150; Max | 10 - 30 | 10 - 30 | 8.5 - 9.0 | < 8.0 | 0.05 ; Max | 8.0 - 9.2 | < 10.0 | 8.0 - 9.2 | < 10.0 | 8.0 - 9.2 | < 10.0 | 8.5 - 9.0 | < 8.0 | 8.0 - 9.2 | < 10.0
Date
2026-09-01 | 6.19 | 1.21 | 0.047 | 0.025 | 0.01 | 0.26 | 8.82 | 10.87 | 0.09 | 0.09 | 1.6 | 8.98 | 8.8 | 0.08 | 0.05 | 1.2 | 0.583 | 0 | 9.28 | 15.14 | 0.04 | 0.07 | 0.94 | 0.806 | 21.6 | 9.3 | 17.04 | 0.02 | 0.09 | 0.52 | 1.13 | 0 | 8.6 | 3.59 | 0.05 | 0.06 | 0.69 | 1.035 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 8.7 | 12.87 | 0.15 | 0.16 | 1.27 |  | 8.42 | 9.83 | 0.14 | 0.11 | 1.42 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 8.42 | 9.83 | 0.14 | 0.11 | 1.42 |  | 10.03 | 147.3 | 2 | 7 | stop | stop | stop | stop | stop | stop | stop | stop | 10.3 | 114.6 | 2 | 10 | 10.54 | 157.9 | 1 | 11 | stop | stop | stop | stop | stop | stop | stop | stop | 10.83 | 595.2 | 46 | 76 | 16 | 3 | 13.5 | 12.8 | 10.9 | 677.3 | 68 | 96 | 40 | 1 | 19.5 | 20.8 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 11.17 | 839.4 | 126 | 154 | 98 | 3 | 24.5 | 14.4 | 8.56 | 6.15 | 0.024 | 8.27 | 5.54 | 8.04 | 5.22 | 8.15 | 6.55 | stop | stop | stop | stop
2026-09-02 | 6.5 | 0.9 | 0.07 | 0.012 | 0.01 | 0.3 | 9.04 | 9.78 | 0.06 | 0.03 | 0.6 | 8.88 | 5.24 | 0.02 | 0.07 | 1.02 | 1.168 | 0 | 8.8 | 5.66 | 0.02 | 0.06 | 0.7 | 1.08 | 21.8 | 9.27 | 18.74 | 0.01 | 0.08 | 0.63 | 1.125 | 0 | 9.54 | 3.28 | 0.02 | 0.05 | 1.12 | 1.13 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 8.31 | 12.79 | 0.05 | 0.1 | 0.8 |  | 8.82 | 7.5 | 0.02 | 0.06 | 0.67 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 8.31 | 12.79 | 0.05 | 0.1 | 0.8 |  | 9.74 | 112.2 | 2 | 8.5 | stop | stop | stop | stop | stop | stop | stop | stop | 8.9 | 67.15 | 1 | 9 | 10.52 | 177.7 | 1 | 14.5 | stop | stop | stop | stop | stop | stop | stop | stop | 10.29 | 268.7 | 20 | 40 | 0 | 1 | 10.5 | 11.2 | 10.91 | 642 | 80 | 104 | 56 | 2 | 19 | 12.8 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 11.15 | 876 | 120 | 148 | 92 | 3 | 25.5 | 12.8 | 8.5 | 5.99 | 0.025 | 8.71 | 5.13 | 8.4 | 5.14 | 8.83 | 5.34 | stop | stop | stop | stop
2026-09-03 | 6.57 | 1.55 | 0.065 | 0.125 | 0.02 | 0.46 | 9.08 | 15.01 | 0.09 | 0.03 | 0.7 | 8.87 | 12.98 | 0.02 | 0.05 | 0.69 | 1.103 | 0 | 8.88 | 11.65 | 0.03 | 0.07 | 0.76 | 0.814 | 21.8 | 8.99 | 6.09 | 0.02 | 0.03 | 0.55 | 0.804 | 0 | 9.45 | 18.28 | 0.02 | 0.05 | 0.78 | 1.198 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 8.52 | 18.31 | 0.07 | 0.07 | 0.83 |  | 8.75 | 26.73 | 0.03 | 0.06 | 1 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 8.52 | 18.31 | 0.07 | 0.07 | 0.83 |  | 9.58 | 202.2 | 2 | 8.5 | stop | stop | stop | stop | stop | stop | stop | stop | 9.14 | 113.1 | 1 | 8.5 | 10.4 | 210.4 | 1 | 15 | stop | stop | stop | stop | stop | stop | stop | stop | 10.25 | 277.3 | 20 | 36 | 4 | 1 | 10 | 16 | 10.93 | 759.6 | 78 | 114 | 42 | 3 | 17.5 | 22.4 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 11.12 | 901.2 | 124 | 142 | 106 | 4 | 24.5 | 19.2 | 8.99 | 6.9 | 0.026 | 8.24 | 9.1 | 8.71 | 6.48 | 8.03 | 4.47 | stop | stop | stop | stop
2026-09-04 | 6.4 | 1.35 | 0.062 | 0.03 | 0.01 | 0.46 | 8.86 | 11.78 | 0.06 | 0.03 | 0.8 | 8.98 | 7.13 | 0.02 | 0.07 | 1.81 | 0.809 | 0 | 8.82 | 8.17 | 0.02 | 0.07 | 0.71 | 1.066 | 21.7 | 8.8 | 6.63 | 0.03 | 0.08 | 0.43 | 0.802 | 0 | 8.71 | 4.31 | 0.02 | 0.1 | 0.58 | 0.921 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 8.46 | 15.57 | 0.06 | 0.1 | 1.2 |  | 8.59 | 16.29 | 0.04 | 0.09 | 0.77 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 8.46 | 15.57 | 0.06 | 0.1 | 1.2 |  | 10.09 | 339.1 | 2 | 10 | stop | stop | stop | stop | 9.43 | 85.37 | 2 | 12 | 9.43 | 124.8 | 2 | 8 | 10.23 | 189.6 | 1 | 14 | stop | stop | stop | stop | stop | stop | stop | stop | 10.45 | 388.3 | 26 | 46 | 6 | 1 | 16 | 11.2 | 10.76 | 502.8 | 44 | 78 | 10 | 2 | 10 | 12.8 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 11.09 | 881 | 96 | 132 | 60 | 3 | 24.5 | 14.4 | 8.52 | 7.16 | 0.026 | 8.31 | 6.54 | 8.23 | 6.29 | 8.83 | 7.16 | stop | stop | stop | stop
2026-09-05 | 6.7 | 1.4 | 0.032 | 0.022 | 0.02 | 0.34 | 8.82 | 9.58 | 0.05 | 0.02 | 0.7 | 8.89 | 13.91 | 0.02 | 0.04 | 0.93 | 1.132 | 0 | 9.01 | 13.75 | 0.02 | 0.05 | 0.58 | 1.125 | 21.9 | 8.98 | 14.49 | 0.01 | 0.07 | 0.36 | 0.627 | 0 | 9.4 | 4.6 | 0.02 | 0.09 | 0.82 | 1.014 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 8.3 | 16.51 | 0.12 | 0.06 | 0.76 |  | 8.38 | 21.37 | 0.06 | 0.12 | 0.76 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 8.3 | 16.51 | 0.06 | 0.12 | 0.76 |  | 9.87 | 364 | 2 | 9 | stop | stop | stop | stop | 10.1 | 154.3 | 3 | 14.5 | stop | stop | stop | stop | 9.99 | 196.5 | 2 | 13.5 | stop | stop | stop | stop | stop | stop | stop | stop | 10.79 | 820.1 | 48 | 80 | 16 | 5 | 35 | 16 | 10.9 | 718.1 | 76 | 102 | 50 | 2 | 17 | 17.6 | 10.92 | 733.1 | 68 | 78 | 38 | 1 | 16.5 | 16 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 11.08 | 860.3 | 104 | 130 | 78 | 4 | 22 | 16 | 8.8 | 6.88 | 0.029 | 8.17 | 6.93 | 8.65 | 7.29 | 8.28 | 4.58 | stop | stop | stop | stop
2026-09-06 | 6.72 | 11.43 | 0.092 | 0.136 | 0.03 | 0.42 | 8.93 | 48.91 | 0.07 | 0.04 | 0.9 | 8.11 | 90.8 | 0.02 | 0.07 | 1.17 | 1.053 | 0 | 7.09 | 59.12 | 0.02 | 0.07 | 0.86 | 0.981 | 21.9 | 9.13 | 15.68 | 0.01 | 0.03 | 0.35 | 0.917 | 0 | 9.07 | 28.06 | 0.01 | 0.04 | 0.21 | 1.166 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 8.87 | 83.17 | 0.07 | 0.08 | 1.41 |  | 9.02 | 101 | 0.18 | 0.08 | 2.16 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 8.87 | 83.17 | 0.07 | 0.08 | 1.41 |  | 9.56 | 887.1 | 3 | 5 | stop | stop | stop | stop | 9.87 | 341.6 | 3 | 13 | stop | stop | stop | stop | 10.22 | 200.4 | 2 | 9.5 | stop | stop | stop | stop | stop | stop | stop | stop | 10.11 | 360.2 | 28 | 48 | 8 | 1 | 16 | 17.6 | 10.92 | 1062 | 74 | 124 | 24 | 2 | 30 | 24 | 10.79 | 1052 | 84 | 144 | 24 | 1 | 29 | 16 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 10.97 | 760 | 112 | 146 | 78 | 4 | 19 | 14.4 | 8.8 | 16.71 | 0.041 | 8.59 | 11.28 | 8.96 | 31.14 | 8.7 | 4.63 | stop | stop | stop | stop
2026-09-07 | 6.75 | 1.96 | 0.022 | 0.025 | 0.01 | 0.44 | 8.71 | 12.92 | 0.04 | 0.01 | 1 | 9.08 | 10.27 | 0.02 | 0.04 | 0.72 | 2.081 | 0 | 9.07 | 9.17 | 0.02 | 0.08 | 0.69 | 1.722 | 22 | 8.95 | 12.6 | 0.01 | 0.04 | 0.52 | 1.686 | 0 | 9.14 | 11.65 | 0.01 | 0.04 | 0.39 | 1.526 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 8.57 | 16.68 | 0.02 | 0.05 | 1.15 |  | 8.9 | 25.17 | 0.02 | 0.04 | 1.64 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 8.57 | 16.68 | 0.02 | 0.05 | 1.15 |  | 9.93 | 173.5 | 1 | 7.5 | stop | stop | stop | stop | 9.82 | 167.7 | 1 | 7.5 | stop | stop | stop | stop | 9.34 | 135.2 | 3 | 7.5 | stop | stop | stop | stop | stop | stop | stop | stop | 11.23 | 2690 | 32 | 60 | 4 | 1 | 175 | 17.6 | 10.77 | 734.8 | 56 | 94 | 18 | 1 | 22 | 14.4 | 10.62 | 652.1 | 52 | 80 | 24 | 1 | 23 | 11.2 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 10.98 | 855.9 | 90 | 120 | 60 | 4 | 23 | 11.2 | 8.78 | 6.66 | 0.024 | 8.99 | 5.42 | 8.84 | 4.75 | 8.61 | 5.39 | stop | stop | stop | stop
2026-09-08 | 6.58 | 1.77 | 0.06 | 0.03 | 0.01 | 0.39 | 8.99 | 14.86 | 0.1 | 0.03 | 0.8 | 8.9 | 6.8 | 0.01 | 0.04 | 1.42 | 1.141 | 0 | 9 | 5.83 | 0.02 | 0.08 | 1.05 | 1.183 | 22.1 | 9.3 | 10.42 | 0.01 | 0.04 | 0.71 | 1.087 | 0 | 9.37 | 21 | 0.02 | 0.06 | 0.51 | 1.2 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 8.48 | 13.54 | 0.01 | 0.02 | 1 |  | 9.08 | 22.83 | 0.02 | 0.03 | 0.8 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 8.48 | 13.54 | 0.01 | 0.02 | 1 |  | 10.28 | 227.5 | 1 | 6 | stop | stop | stop | stop | 9.22 | 129.8 | 1 | 5.5 | stop | stop | stop | stop | 10.27 | 173.8 | 2 | 15 | stop | stop | stop | stop | stop | stop | stop | stop | 10.4 | 367.2 | 22 | 38 | 6 | 2 | 12 | 6.4 | 10.74 | 643.5 | 56 | 86 | 26 | 3 | 21 | 12.8 | 10.85 | 736.9 | 70 | 98 | 42 | 3 | 15 | 12.8 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 10.96 | 896.2 | 92 | 126 | 58 | 5 | 19 | 17.6 | 8.6 | 5.5 | 0.027 | 8.51 | 5.35 | 8.43 | 4.69 | 8.72 | 6.71 | stop | stop | stop | stop
2026-09-09 | 6.51 | 1.47 | 0.072 | 0.149 | 0.01 | 0.41 | 9.36 | 14.37 | 0.04 | 0.02 | 1.2 | 9.28 | 7.19 | 0.02 | 0.04 | 0.87 | 0.899 | 0 | 8.94 | 6.58 | 0.02 | 0.08 | 0.56 | 1.571 | 22 | 9.02 | 11.45 | 0.01 | 0.05 | 0.59 | 1.016 | 0 | 9.1 | 2.36 | 0.02 | 0.05 | 0.45 | 1.118 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 8.68 | 12.36 | 0.03 | 0.07 | 0.61 |  | 9.11 | 21.81 | 0.04 | 0.14 | 0.69 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 8.68 | 12.36 | 0.03 | 0.07 | 0.61 |  | 10.16 | 163.8 | 2 | 6.5 | stop | stop | stop | stop | 9.4 | 106.3 | 2 | 9 | stop | stop | stop | stop | 9.91 | 159.6 | 4 | 18 | stop | stop | stop | stop | stop | stop | stop | stop | 10.11 | 146.5 | 24 | 28 | 20 | 4 | 9 | 27.2 | 10.83 | 622.4 | 52 | 96 | 18 | 2 | 13 | 28.8 | 10.91 | 751.7 | 68 | 108 | 28 | 1 | 13 | 28.8 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 11.01 | 797.4 | 84 | 118 | 500 | 4 | 19 | 12.8 | 8.5 | 4.12 | 0.021 | 8.87 | 3.71 | 8.63 | 3.62 | 8.09 | 5.43 | stop | stop | stop | stop
2026-09-10 | 6.54 | 1.25 | 0.013 | 0.031 | 0.01 | 0.37 | 8.39 | 3.86 | 0.05 | 0.02 | 1.1 | 9.06 | 6.51 | 0.02 | 0.1 | 1.59 | 0.898 | 0 | 9.25 | 15.46 | 0.01 | 0.02 | 1.47 | 0.93 | 21.9 | 8.94 | 6.43 | 0.02 | 0.02 | 0.58 | 0.808 | 0 | 9.16 | 19 | 0.03 | 0.06 | 0.55 | 0.806 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 8.31 | 16.79 | 0.03 | 0.15 | 2.43 |  | 8.63 | 31.3 | 0.02 | 0.05 | 1.86 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 8.31 | 16.79 | 0.03 | 0.15 | 2.43 |  | stop | stop | stop | stop | stop | stop | stop | stop | 9.82 | 107.8 | 1 | 8.5 | 9.95 | 97.08 | 2 | 8 | 10.21 | 143.7 | 4 | 15 | stop | stop | stop | stop | stop | stop | stop | stop | 10.91 | 632 | 44 | 78 | 10 | 2 | 20 | 20.8 | stop | stop | stop | stop | stop | stop | stop | stop | 11.12 | 905.1 | 100 | 170 | 30 | 2 | 27 | 28.8 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 11.09 | 703.5 | 80 | 112 | 48 | 3 | 18 | 12.8 | stop | stop | stop | 8.23 | 3.89 | 8.46 | 3.96 | 8.37 | 4.03 | stop | stop | stop | stop
2026-09-11 | 6.38 | 1.55 | 0.039 | 0.03 | 0.01 | 0.36 | 8.78 | 16.32 | 0.05 | 0.02 | 0.7 | 9.12 | 24.8 | 0.02 | 0.06 | 1.25 | 0.908 | 0 | 9.2 | 17.43 | 0.01 | 0.03 | 1.22 | 0.801 | 22.3 | 8.89 | 6.41 | 0.02 | 0.03 | 0.36 | 2.157 | 0 | 9.2 | 11.55 | 0.01 | 0.02 | 0.44 | 1.157 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 8.44 | 13.75 | 0.02 | 0.04 | 1.28 |  | 8.36 | 18.75 | 0.03 | 0.07 | 1.01 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 8.44 | 13.75 | 0.02 | 0.04 | 1.28 |  | stop | stop | stop | stop | stop | stop | stop | stop | 10.05 | 163.7 | 2 | 13 | 9.55 | 88.51 | 2 | 12 | 9.89 | 116.5 | 6 | 14 | stop | stop | stop | stop | stop | stop | stop | stop | 10.5 | 271.4 | 26 | 38 | 14 | 1 | 10 | 11.2 | stop | stop | stop | stop | stop | stop | stop | stop | 10.77 | 619.9 | 66 | 106 | 26 | 2 | 20 | 28.8 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 11 | 722.5 | 86 | 128 | 64 | 4 | 18 | 11.2 | stop | stop | stop | 8.22 | 3.68 | 8.43 | 4.12 | 8.63 | 5.75 | stop | stop | stop | stop
2026-09-12 | 6.4 | 1.24 | 0.074 | 0.004 | 0.02 | 0.27 | 8.5 | 4.01 | 0.13 | 0.01 | 0.7 | 8.91 | 7.43 | 0.02 | 0.06 | 0.81 | 0.837 | 0 | 8.85 | 6.22 | 0.02 | 0.06 | 0.78 | 0.548 | 22 | 8.82 | 5.5 | 0.03 | 0.1 | 0.36 | 0.939 | 0 | 9.37 | 35.56 | 0.03 | 0.1 | 0.51 | 1.031 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 8.36 | 6.34 | 0.06 | 0.19 | 0.8 |  | 8.52 | 12.94 | 0.03 | 0.08 | 0.87 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 8.36 | 6.34 | 0.06 | 0.19 | 0.8 |  | stop | stop | stop | stop | stop | stop | stop | stop | 9.73 | 84.9 | 2 | 6.5 | 9.92 | 87.03 | 1 | 6.5 | 10.3 | 146.5 | 4 | 12 | stop | stop | stop | stop | stop | stop | stop | stop | 10.99 | 1063 | 102 | 144 | 60 | 3 | 10 | 16 | stop | stop | stop | stop | stop | stop | stop | stop | 10.73 | 527.7 | 48 | 84 | 12 | 3 | 15 | 28.8 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 11.02 | 671 | 82 | 108 | 56 | 4 | 13 | 14.4 | stop | stop | stop | 8.23 | 3.29 | 8.59 | 3.68 | 8.14 | 4.35 | stop | stop | stop | stop
2026-09-13 | 6.55 | 0.81 | 0.047 | 0.128 | 0.01 | 0.23 | 9.1 | 9.19 | 0.03 | 0.03 | 0.6 | 8.98 | 6.64 | 0.02 | 0.06 | 0.63 | 0.801 | 0 | 9.16 | 6.33 | 0.02 | 0.06 | 0.59 | 0.803 | 22.2 | 8.98 | 9.45 | 0.02 | 0.1 | 0.29 | 0.802 | 0 | 9.28 | 5.79 | 0.02 | 0.06 | 0.99 | 0.806 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 8.89 | 12.3 | 0.04 | 0.04 | 0.89 |  | 9.14 | 14.06 | 0.02 | 0.06 | 0.65 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 8.89 | 12.3 | 0.04 | 0.04 | 0.89 |  | stop | stop | stop | stop | stop | stop | stop | stop | 11 | 423 | 2 | 14 | 10.43 | 156.2 | 1 | 13.5 | 10.07 | 150.4 | 6 | 13.5 | stop | stop | stop | stop | stop | stop | stop | stop | 10.98 | 885.3 | 82 | 132 | 32 | 4 | 13 | 11.2 | stop | stop | stop | stop | stop | stop | stop | stop | 10.86 | 584.4 | 54 | 98 | 10 | 3 | 22.5 | 22.4 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 11.09 | 600.4 | 74 | 98 | 50 | 3 | 15.5 | 12.8 | 8.9 | 3.85 | 0.018 | 9.09 | 10.61 | 8.26 | 4.13 | 8.82 | 4.5 | stop | stop | stop | stop
2026-09-14 | 6.33 | 0.78 | 0.084 | 0.01 | 0.04 | 0.27 | 8.89 | 7.58 | 0.11 | 0.03 | 0.7 | 9.3 | 23.1 | 0.01 | 0.04 | 0.74 | 1.107 | 0 | 9.28 | 20.96 | 0.01 | 0.05 | 0.54 | 1.164 | 22.2 | 9.3 | 12.44 | 0.02 | 0.1 | 0.37 | 0.807 | 0 | 9.23 | 24.82 | 0.01 | 0.06 | 0.63 | 1.028 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 9.14 | 14.44 | 0.02 | 0.1 | 0.58 |  | 9.09 | 14.47 | 0.03 | 0.07 | 0.72 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 9.14 | 14.44 | 0.02 | 0.1 | 0.58 |  | stop | stop | stop | stop | stop | stop | stop | stop | 10.85 | 294.4 | 2 | 11 | 10.29 | 133.2 | 2 | 11.5 | 10.9 | 330.3 | 6 | 15 | stop | stop | stop | stop | stop | stop | stop | stop | 11.14 | 1223 | 126 | 160 | 92 | 3 | 16 | 12.8 | stop | stop | stop | stop | stop | stop | stop | stop | 11.06 | 768.7 | 100 | 140 | 60 | 4 | 30 | 24 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 11.04 | 643.3 | 100 | 124 | 76 | 3 | 24 | 11.2 | 7.86 | 4.28 | 0.021 | 8.64 | 5.22 | 8.38 | 4.2 | 8.63 | 4.48 | stop | stop | stop | stop
2026-09-15 | 6.6 | 1.31 | 0.067 | 0.033 | 0.03 | 0.5 | 8.53 | 11.47 | 0.1 | 0.05 | 0.7 | 9.24 | 19.82 | 0.03 | 0.08 | 0.92 | 1.11 | 0 | 9.27 | 14.42 | 0.02 | 0.07 | 0.75 | 0.823 | 22.2 | 8.86 | 11.17 | 0.02 | 0.05 | 0.36 | 1.147 | 0 | 9.08 | 24.91 | 0.02 | 0.07 | 0.59 | 1.2 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 8.99 | 21.71 | 0.04 | 0.08 | 0.79 |  | 9.11 | 43.95 | 0.07 | 1.24 | 0.74 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 8.99 | 21.71 | 0.04 | 0.08 | 0.79 |  | stop | stop | stop | stop | stop | stop | stop | stop | 10.4 | 225.6 | 1 | 6 | 9.83 | 125.9 | 2 | 7.5 | 10.92 | 541 | 4 | 13 | stop | stop | stop | stop | stop | stop | stop | stop | 10.9 | 877 | 74 | 72 | 76 | 2 | 23 | 12.8 | stop | stop | stop | stop | stop | stop | stop | stop | 10.95 | 693 | 74 | 92 | 56 | 2 | 17 | 12.8 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 11.02 | 775.4 | 88 | 102 | 74 | 4 | 25 | 12.8 | 8.76 | 5.82 | 0.019 | 8.16 | 6.36 | 8.5 | 5.24 | 8.01 | 4.55 | stop | stop | stop | stop
2026-09-16 | 6.27 | 0.88 | 0.048 | 0.071 | 0.03 | 0.24 | 9.42 | 31.17 | 0.03 | 0.03 | 0.7 | 8.81 | 7.1 | 0.03 | 0.06 | 0.73 | 1.102 | 0 | 9.3 | 9.58 | 0.05 | 0.07 | 1 | 0.963 |  | 9.21 | 18.17 | 0.05 | 0.09 | 0.68 | 0.806 | 0 | 9.27 | 22.16 | 0.02 | 0.1 | 0.6 | 1.178 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 9.4 | 26.43 | 0.01 | 0.05 | 0.74 |  | 9.21 | 34.65 | 0.03 | 0.02 | 0.88 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 9.4 | 26.43 | 0.01 | 0.05 | 0.74 |  | stop | stop | stop | stop | 10.79 | 343.7 | 1 | 8.5 | stop | stop | stop | stop | 9.64 | 63.28 | 1 | 9 | 10.85 | 463.6 | 2 | 11 | stop | stop | stop | stop | stop | stop | stop | stop | 10.86 | 777.4 | 70 | 86 | 54 | 2 | 16 | 11.2 | stop | stop | stop | stop | stop | stop | stop | stop | 11.03 | 805.3 | 82 | 104 | 60 | 1 | 30 | 14.4 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 11.01 | 729.2 | 80 | 96 | 64 | 3 | 22 | 8 | 8.01 | 4.73 | 0.01 | 8.62 | 6.4 | 8.9 | 4.96 | 7.78 | 5.24 | stop | stop | stop | stop
2026-09-17 | 6.38 | 1.29 | 0.03 | 0.054 | 0.04 | 0.46 | 8.27 | 10.02 | 0.06 | 0.03 | 1.5 | 9.17 | 2.18 | 0.03 | 0.07 | 1.43 | 1.126 | 0 | 9.28 | 17.05 | 0.01 | 0.1 | 0.73 | 0.815 | 21.6 | 9.27 | 17.19 | 0.03 | 0.08 | 0.55 | 0.9 | 0 | 9.21 | 24.12 | 0.01 | 0.03 | 0.63 | 1.185 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 8.92 | 14.12 | 0.03 | 0.03 | 1.65 |  | 8.67 | 33.99 | 0.02 | 0.13 | 1.44 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 8.92 | 14.12 | 0.03 | 0.03 | 1.65 |  | stop | stop | stop | stop | 10.98 | 499.9 | 3 | 6 | stop | stop | stop | stop | 10.34 | 108.6 | 1 | 5 | 10.95 | 618.3 | 4 | 11.5 | stop | stop | stop | stop | stop | stop | stop | stop | 11.28 | 1680 | 136 | 168 | 104 | 5 | 30 | 11.2 | stop | stop | stop | stop | stop | stop | stop | stop | 11.09 | 872.4 | 88 | 122 | 54 | 2 | 30 | 16 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 11.08 | 743 | 74 | 98 | 50 | 3 | 19 | 6.4 | 8.39 | 6.43 | 0.01 | 7.89 | 5.63 | 8.56 | 6.03 | 7.34 | 4.91 | stop | stop | stop | stop
2026-09-18 | 6.4 | 1 | 0.092 | 0.05 | 0.03 | 0.28 | 8.68 | 6.89 | 0.06 | 0.03 | 1.7 | 9.01 | 15.23 | 0.04 | 0.02 | 1.23 | 0.893 | 0 | 9.09 | 8.08 | 0.03 | 0.1 | 0.54 | 1.122 |  | 8.81 | 4.6 | 0.03 | 0.06 | 0.3 | 0.822 | 0 | 9.13 | 6.96 | 0.01 | 0.06 | 0.62 | 1.103 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 9 | 19.55 | 0.02 | 0.07 | 0.79 |  | 9.08 | 29.63 | 0.03 | 0.02 | 0.95 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 9 | 19.55 | 0.02 | 0.07 | 0.79 |  | stop | stop | stop | stop | 10.13 | 146.8 | 1 | 8.52 | stop | stop | stop | stop | 9.79 | 74.97 | 1 | 5 | 10.97 | 532.7 | 2 | 10.5 | stop | stop | stop | stop | stop | stop | stop | stop | 10.87 | 882.1 | 76 | 82 | 70 | 4 | 13 | 16 | stop | stop | stop | stop | stop | stop | stop | stop | 10.75 | 524.3 | 56 | 76 | 36 | 1 | 19 | 22.4 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 10.94 | 647.2 | 86 | 96 | 76 | 1 | 16 | 11.2 | 8.52 | 4.98 | 0.027 | 8.64 | 4.79 | 8.87 | 5.21 | 8.41 | 4.35 | stop | stop | stop | stop
2026-09-19 | 6.31 | 0.96 | 0.038 | 0.123 | 0.01 | 0.24 | 9.45 | 7.86 | 0.04 | 0.03 | 1.2 | 9.28 | 19.96 | 0.02 | 0.08 | 0.64 | 0.807 | 0 | 9.26 | 11.74 | 0.02 | 0.02 | 0.46 | 0.85 | 21.9 | 9.09 | 4.44 | 0.01 | 0.08 | 0.31 | 0.803 | 0 | 8.83 | 5.97 | 0.02 | 0.09 | 0.51 | 1.036 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 9.48 | 24.57 | 0.02 | 0.06 | 0.78 |  | 9.56 | 36.06 | 0.05 | 0.04 | 2.45 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 9.48 | 24.57 | 0.02 | 0.06 | 0.78 |  | stop | stop | stop | stop | 10.43 | 154.2 | 4 | 7 | stop | stop | stop | stop | 10.02 | 105.5 | 4 | 8 | 10.92 | 451.5 | 4 | 11.5 | stop | stop | stop | stop | stop | stop | stop | stop | 10.59 | 493 | 26 | 46 | 6 | 2 | 7 | 11.2 | stop | stop | stop | stop | stop | stop | stop | stop | 10.8 | 506.9 | 48 | 68 | 28 | 1 | 7 | 17.6 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 11.09 | 707.6 | 66 | 102 | 30 | 3 | 16.5 | 11.2 | 8.25 | 4.88 | 0.031 | 8.28 | 6.42 | 8.7 | 4.97 | 9 | 4.94 | stop | stop | stop | stop
2026-09-20 | 6.41 | 0.99 | 0.058 | 0.081 | 0.01 | 0.63 | 8.58 | 3.31 | 0.06 | 0.02 | 1.5 | 9.25 | 5.61 | 0.02 | 0.07 | 1.4 | 1.143 | 0 | 9.29 | 7.37 | 0.02 | 0.07 | 1.43 | 0.853 | 22 | 9.06 | 4.48 | 0.01 | 0.08 | 0.57 | 1.098 | 0 | 9.55 | 25 | 0.02 | 0.09 | 0.69 | 1.175 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 8.07 | 12.68 | 0.02 | 0.08 | 0.64 |  | 8.3 | 26.84 | 0.03 | 0.08 | 0.64 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 8.07 | 12.68 | 0.02 | 0.08 | 0.64 |  | stop | stop | stop | stop | 10.02 | 112.5 | 2 | 7 | stop | stop | stop | stop | 9.83 | 70.81 | 2 | 8 | 10.98 | 443.9 | 6 | 10 | stop | stop | stop | stop | stop | stop | stop | stop | 10.38 | 283 | 40 | 0 | 0 | 1 | 10 | 12.8 | stop | stop | stop | stop | stop | stop | stop | stop | 10.96 | 661.7 | 54 | 96 | 12 | 4 | 30 | 28.8 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 11.13 | 768.1 | 82 | 106 | 58 | 6 | 22 | 12.8 | 8.95 | 5.91 | 0.028 | 9 | 4.61 | 8.77 | 4.34 | 8.71 | 3.8 | stop | stop | stop | stop
2026-09-21 | 6.52 | 1 | 0.032 | 0.042 | 0.02 | 0.42 | 8.47 | 3.55 | 0.02 | 0.075 | 1.1 | 9.02 | 5.25 | 0.01 | 0.03 | 0.82 | 1.143 | 0 | 9.16 | 6.12 | 0.02 | 0.04 | 0.54 | 0.84 | 22.1 | 9.06 | 4.65 | 0.02 | 0.04 | 0.54 | 1.2 | 0 | 9.35 | 17.91 | 0.02 | 0.02 | 0.42 | 1.128 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.94 | 18.39 | 0.04 | 0.02 | 2.22 |  | 8.15 | 10.08 | 0.01 | 0.06 | 1.05 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 7.94 | 18.39 | 0.04 | 0.02 | 2.22 |  | stop | stop | stop | stop | 9.52 | 85.12 | 3 | 7.5 | stop | stop | stop | stop | 9.34 | 47.57 | 3 | 6 | 10.88 | 363.9 | 4 | 10 | stop | stop | stop | stop | stop | stop | stop | stop | 11.28 | 2380 | 154 | 226 | 82 | 6 | 66 | 41.6 | stop | stop | stop | stop | stop | stop | stop | stop | 10.85 | 600.1 | 46 | 78 | 14 | 2 | 28 | 17.6 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 11 | 785.6 | 80 | 108 | 52 | 5 | 19 | 14.4 | 8.7 | 6.48 | 0.018 | 8.54 | 4.26 | 8.45 | 4.23 | 8.42 | 16.12 | stop | stop | stop | stop
2026-09-22 | 6.4 | 0.95 | 0.038 | 0.092 | 0.02 | 0.36 | 9.44 | 78.19 | 0.05 | 0.07 | 1.4 | 8.95 | 6.48 | 0.01 | 0.09 | 1.05 | 1.161 | 0 | 9.02 | 7.17 | 0.01 | 0.04 | 0.56 | 1.098 | 22.1 | 8.8 | 4.52 | 0.01 | 0.03 | 0.32 | 0.997 | 0 | 8.59 | 3.25 | 0.01 | 0.04 | 0.4 | 0.945 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 8.62 | 4.07 | 0.02 | 0.06 | 0.75 |  | 8.97 | 17.03 | 0.01 | 0.05 | 0.56 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 8.62 | 4.07 | 0.02 | 0.06 | 0.75 |  | stop | stop | stop | stop | 10.45 | 164 | 2 | 8 | stop | stop | stop | stop | 10.14 | 107.3 | 3 | 10.5 | 10.91 | 354.7 | 4 | 10 | stop | stop | stop | stop | stop | stop | stop | stop | 10.22 | 192.7 | 12 | 22 | 2 | 1 | 18 | 11.2 | stop | stop | stop | stop | stop | stop | stop | stop | 10.85 | 325.8 | 50 | 84 | 16 | 2 | 30 | 19.2 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 11.03 | 363.8 | 74 | 102 | 46 | 4 | 22 | 11.2 | 8.64 | 5.87 | 0.015 | 8.67 | 5.51 | 8.71 | 5.6 | 8.9 | 5.17 | stop | stop | stop | stop
2026-09-23 | 6.3 | 0.97 | 0.049 | 0.066 | 0.01 | 0.36 | 8.66 | 4.84 | 0.04 | 0.01 | 1.3 | 8.91 | 6.14 | 0.01 | 0.03 | 0.74 | 0.867 | 0 | 8.81 | 6.01 | 0.01 | 0.09 | 0.52 | 4.339 | 22.4 | 9.05 | 4.64 | 0.01 | 0.1 | 0.34 | 0.87 | 0 | 8.49 | 3.05 | 0.01 | 0.03 | 0.53 | 1.143 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 8.55 | 14.55 | 0.02 | 0.02 | 2.12 |  | 8.7 | 10 | 0.04 | 0.02 | 0.74 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 8.55 | 14.55 | 0.02 | 0.02 | 2.12 |  | stop | stop | stop | stop | 10.32 | 160.9 | 3 | 10 | stop | stop | stop | stop | 9.82 | 88.97 | 3 | 9.5 | 10.94 | 344.2 | 4 | 10.5 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 10.96 | 745.7 | 72 | 104 | 40 | 3 | 22 | 19.2 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 11.17 | 733.9 | 88 | 112 | 64 | 3 | 21 | 11.2 | 8.56 | 6.28 | 0.024 | 8.68 | 4.44 | 8.79 | 4.35 | 8.88 | 6.24 | stop | stop | stop | stop
2026-09-24 | 6.49 | 0.85 | 0.038 | 0.067 | 0.02 | 0.66 | 8.67 | 4.08 | 0.02 | 0.03 | 1 | 8.98 | 4.76 | 0.01 | 0.06 | 1.16 | 1.101 | 0 | 9.21 | 16.88 | 0.01 | 0.03 | 0.66 | 1.199 | 22.1 | 9.08 | 18.98 | 0.03 | 0.03 | 0.45 | 0.848 | 0 | 9.33 | 22.2 | 0.03 | 0.09 | 1.08 | 1.096 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 8.62 | 74.56 | 0.02 | 0.06 | 1.08 |  | 8.43 | 19.44 | 0.03 | 0.04 | 0.69 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 8.62 | 74.56 | 0.02 | 0.06 | 1.08 |  | 10.6 | 224.3 | 4 | 15 | 10.46 | 142.2 | 2 | 9.5 | stop | stop | stop | stop | 9.81 | 81.34 | 3 | 10.5 | 10.85 | 289.2 | 4 | 10.5 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 10.88 | 632.2 | 58 | 88 | 28 | 3 | 16 | 16 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 10.89 | 810.1 | 80 | 110 | 50 | 3 | 18 | 11.2 | 8.53 | 5.31 | 0.016 | 8.25 | 4.49 | 8.27 | 5.19 | stop | stop | stop | stop | stop | stop
2026-09-25 | 6.45 | 0.94 | 0.021 | 0.024 | 0.02 | 0.76 | 8.72 | 15.21 | 0.03 | 0.01 | 0.9 | 8.96 | 5.67 | 0.02 | 0.1 | 0.91 | 1.126 | 0 | 9.09 | 4.03 | 0.02 | 0.09 | 0.7 | 1.051 | 22.4 | 8.86 | 3.67 | 0.01 | 0.1 | 0.39 | 0.898 | 0 | 9.42 | 1.99 | 0.01 | 0.07 | 0.48 | 1.195 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 8.6 | 59.19 | 0.02 | 0.05 | 1.35 |  | 8.48 | 4.73 | 0.01 | 0.13 | 1.02 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 8.6 | 59.19 | 0.02 | 0.05 | 1.35 |  | 10.68 | 277.7 | 2 | 10.5 | 10.66 | 202.1 | 2 | 8.5 | stop | stop | stop | stop | 10.15 | 111.6 | 2 | 15 | 10.78 | 262.3 | 3 | 10.5 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 10.72 | 596.7 | 52 | 80 | 24 | 2 | 23 | 17.6 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 10.86 | 884.4 | 80 | 110 | 50 | 4 | 16 | 20.8 | 8.57 | 4.31 | 0.02 | 8.57 | 7.77 | 8.43 | 6.58 | stop | stop | stop | stop | stop | stop
2026-09-26 | 6.57 | 0.87 | 0.02 | 0.068 | 0.01 | 0.28 | 8.46 | 2.12 | 0.02 | 0.01 | 0.8 | 8.22 | 3.9 | 0.01 | 0.05 | 0.73 | 1.173 | 0 | 8.05 | 3.66 | 0.01 | 0.08 | 0.55 | 0.875 | 22.2 | 8.01 | 3.6 | 0.01 | 0.04 | 0.41 | 1.063 | 0 | 8.09 | 1.69 | 0.01 | 0.1 | 0.38 | 1.025 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 7.92 | 54.4 | 0.03 | 0.03 | 2.02 |  | 8.32 | 17.84 | 0.01 | 0.06 | 0.61 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 7.92 | 54.4 | 0.03 | 0.03 | 2.02 |  | 10.57 | 245.5 | 2 | 7.5 | 10.78 | 281.4 | 2 | 8.5 | stop | stop | stop | stop | 10.49 | 169.6 | 2 | 11 | 10.71 | 237.9 | 2 | 10 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 10.94 | 559 | 58 | 90 | 26 | 2 | 23 | 16 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 11 | 714.4 | 64 | 98 | 30 | 3 | 19 | 25.6 | 8.86 | 4.88 | 0.017 | 8.71 | 3.57 | 8.56 | 3.23 | stop | stop | stop | stop | stop | stop
2026-09-27 | 6.48 | 0.67 | 0.031 | 0.037 | 0.02 | 0.22 | 8.34 | 3.28 | 0.06 | 0.02 | 0.9 | 8.8 | 7.95 | 0.04 | 0.06 | 1.2 | 0.809 | 0 | 8.85 | 17.19 | 0.05 | 0.02 | 0.98 | 0.843 | 22.4 | 8.8 | 15.1 | 0.05 | 0.08 | 0.36 | 0.816 | 0 | 9.3 | 20.91 | 0.04 | 0.06 | 0.57 | 0.811 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop |  | 8.85 | 21.11 | 0.01 | 0.11 | 0.86 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 9.11 | 34.68 | 0.04 | 0.02 | 1.14 |  | 10.69 | 272.8 | 1 | 10 | 10.94 | 202.4 | 1 | 5 | stop | stop | stop | stop | 10.76 | 122.3 | 1 | 5 | 10.9 | 310.8 | 2 | 9.5 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 11.07 | 649.7 | 66 | 98 | 34 | 2 | 17 | 17.6 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 10.84 | 746.1 | 58 | 98 | 18 | 4 | 23 | 22.4 | 8.5 | 3.47 | 0.046 | 8.61 | 3.57 | 9.08 | 3.44 | stop | stop | stop | stop | stop | stop
2026-09-28 | 6.16 | 0.78 | 0.031 | 0.102 | 0.02 | 0.33 | 8.31 | 13.41 | 0.04 | 0.02 | 1.1 | 9.25 | 20.42 | 0.01 | 0.07 | 1.09 | 0.856 | 0 | 8.81 | 14.56 | 0.02 | 0.1 | 0.98 | 0.899 | 22.7 | 8.89 | 19.36 | 0.01 | 0.05 | 0.47 | 0.875 | 0 | 9.31 | 21.08 | 0.01 | 0.05 | 0.78 | 0.866 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop |  | 8.9 | 18.97 | 0.02 | 0.033 | 1.01 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 8.68 | 21.19 | 0.03 | 0.06 | 1.22 |  | 10.65 | 200.6 | 3 | 7 | 10.01 | 77.89 | 1 | 6.5 | stop | stop | stop | stop | 10.65 | 30.59 | 1 | 9 | 11.03 | 409.4 | 5 | 13 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 10.96 | 636.6 | 60 | 96 | 24 | 3 | 18 | 28.8 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 10.98 | 734.1 | 92 | 116 | 68 | 4 | 23 | 24 | 8.42 | 5.5 | 0.026 | 8.38 | 4.37 | 7.87 | 4.24 | stop | stop | stop | stop | stop | stop
2026-09-29 | 6.55 | 0.83 | 0.036 | 0.033 | 0.01 | 0.5 | 9.7 | 19.43 | 0.05 | 0.03 | 1.1 | 9.25 | 5.58 | 0.02 | 0.1 | 1.8 | 1.06 | 0 | 9.25 | 16.78 | 0.02 | 0.07 | 1.42 | 0.804 | 22.7 | 9.16 | 14.13 | 0.01 | 0.07 | 0.8 | 0.801 | 0 | 9.28 | 22.56 | 0.01 | 0.1 | 1.05 | 1.198 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop |  | 9.03 | 15.05 | 0.02 | 0.04 | 1.08 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 8.63 | 13.33 | 0.03 | 0.15 | 1.6 |  | 10.76 | 236.1 | 3 | 8.5 | 10.33 | 124.4 | 2 | 10 | stop | stop | stop | stop | 10.13 | 88.98 | 2 | 13 | 10.74 | 412.4 | 4 | 13 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 10.9 | 464.2 | 56 | 86 | 26 | 3 | 30 | 19.2 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 10.98 | 721.9 | 74 | 106 | 42 | 4 | 21.5 | 27.2 | 8.58 | 4.91 | 0.016 | 8.61 | 4.43 | 9.06 | 4.44 | stop | stop | stop | stop | stop | stop
2026-09-30 | [6 empty] | 9.39 | 12.23 | 0.06 | 0.03 | 0.9 | 9.16 | 20.71 | 0.02 | 0.1 | 1.42 | 1.108 | 0 | 9.14 | 20.48 | 0.01 | 0.1 | 1.03 | 1.187 | 22.7 | 8.9 | 17.25 | 0.02 | 0.06 | 0.36 | 1.103 | 0 | 8.95 | 27.69 | 0.01 | 0.07 | 0.77 | 1.12 | 0 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop |  | 9.07 | 17.57 | 0.03 | 0.16 | 2.95 |  | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | 8.48 | 8.57 | 0.04 | 0.06 | 1.11 |  | 10.1 | 85.06 | 1 | 8 | 9.62 | 60.79 | 2 | 5.5 | stop | stop | stop | stop | 9.03 | 61.15 | 3 | 14 | 10.86 | 342.6 | 8 | 12 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 10.99 | 558.8 | 79 | 123.2 | 24.8 | 4 | 30 | 11.2 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 11.14 | 740.1 | 82.2 | 126.2 | 38.2 | 4 | 21 | 17.6 | 9 | 4.31 | 0.032 | 8.86 | 4.35 | 8.69 | 3.86 | stop | stop | stop | stop | stop | stop
2026-10-01
| DEMIN TANK 2000 MT | [5 empty] | CONDENSATE TANK 200 MT |  |  |  |  | BFW PP#1 | [6 empty] | BFW PP#2 | [6 empty] | BFW PP#3 | [6 empty] | BFW CFBC | [6 empty] | BFW HP Coal | [6 empty] | BFW HP Gas | [6 empty] | BFW MP | [5 empty] | BFW TOH #3/#4 | [5 empty] | BFW HRSG GT #1 | [5 empty] | BFW HRSG GT #2 | [5 empty] | BFW OMNICAL | [5 empty] | Boiler PP #1 |  |  |  | Boiler PP #2 |  |  |  | Boiler PP #3 |  |  |  | Boiler PP #4 |  |  |  | Boiler CFBC |  |  |  | Boiler HP Coal |  |  |  | Boiler HP Gas |  |  |  | Boiler MP | [7 empty] | Boiler HRSG TOH #3 | [7 empty] | Boiler HRSG TOH #4 | [7 empty] | Boiler HRSG GT #1 | [7 empty] | Boiler HRSG GT #2 | [7 empty] | Boiler OMNICAL | [7 empty] | Condensate Turbin #3 |  |  | Condensate Header MPS - PP |  | Condensate Header LPS - PP |  | Condensate Header MPS - BH |  | Condensate Header HPS - BH |  | Condensate Header MPS - GT
Parameter | pH | Conductivity | T. Hardness | Silica | Iron |  | pH | Conductivity | T. Hardness | Iron | Turbidity | pH | Conductivity | Iron | T. Hardness | Turbidity | Surgard | DO | pH | Conductivity | Iron | T. Hardness | Turbidity | Surgard | DO | pH | Conductivity | Iron | T. Hardness | Turbidity | Surgard | DO | pH | Conductivity | Iron | T. Hardness | Turbidity | Surgard | DO | pH | Conductivity | Iron | T. Hardness | Turbidity | Surgard | DO | pH | Conductivity | Iron | T. Hardness | Turbidity | Surgard | DO | pH | Conductivity | Iron | T. Hardness | Turbidity | DO | pH | Conductivity | Iron | T. Hardness | Turbidity | DO | pH | Conductivity | Iron | T. Hardness | Turbidity | DO | pH | Conductivity | Iron | T. Hardness | Turbidity | DO | pH | Conductivity | Iron | T. Hardness | Turbidity | DO | pH | Conductivity | Silica | Phosphate | pH | Conductivity | Silica | Phosphate | pH | Conductivity | Silica | Phosphate | pH | Conductivity | Silica | Phosphate | pH | Conductivity | Silica | Phosphate | pH | Conductivity | Silica | Phosphate | pH | Conductivity | Silica | Phosphate | pH | Conductivity | P - Alkalinity | M - Alkalinity | O - Alkalinity | Silica | Phosphate | Sulphite | pH | Conductivity | P - Alkalinity | M - Alkalinity | O - Alkalinity | Silica | Phosphate | Sulphite | pH | Conductivity | P - Alkalinity | M - Alkalinity | O - Alkalinity | Silica | Phosphate | Sulphite | pH | Conductivity | P - Alkalinity | M - Alkalinity | O - Alkalinity | Silica | Phosphate | Sulphite | pH | Conductivity | P - Alkalinity | M - Alkalinity | O - Alkalinity | Silica | Phosphate | Sulphite | pH | Conductivity | P - Alkalinity | M - Alkalinity | O - Alkalinity | Silica | Phosphate | Sulphite | pH | Conductivity | Silica | pH | Conductivity | pH | Conductivity | pH | Conductivity | pH | Conductivity | pH | Conductivity
|  | (µS/cm) | (ppm CaCO3) | (ppm SiO2) | (ppm Fe) |  |  | (µS/cm) | (ppm CaCO3) | (ppm Fe) | (NTU) |  | (µS/cm) | (ppm Fe) | (ppm CaCO3) | NTU | (ppm surgard) | (ppb) |  | (µS/cm) | (ppm Fe) | (ppm CaCO3) | NTU | (ppm surgard) | (ppb) |  | (µS/cm) | (ppm Fe) | (ppm CaCO3) | NTU | (ppm surgard) | (ppb) |  | (µS/cm) | (ppm Fe) | (ppm CaCO3) | NTU | (ppm surgard) | (ppb) |  | (µS/cm) | (ppm Fe) | (ppm CaCO3) | NTU | (ppm surgard) | (ppb) |  | (µS/cm) | (ppm Fe) | (ppm CaCO3) | NTU | (ppm surgard) | (ppb) |  | (µS/cm) | (ppm Fe) | (ppm CaCO3) | NTU | (ppb) |  | (µS/cm) | (ppm Fe) | (ppm CaCO3) | NTU | (ppb) |  | (µS/cm) | (ppm Fe) | (ppm CaCO3) | NTU | (ppb) |  | (µS/cm) | (ppm Fe) | (ppm CaCO3) | NTU | (ppb) |  | (µS/cm) | (ppm Fe) | (ppm CaCO3) | NTU | (ppb) |  | (µS/cm) | (ppm SiO2) | ppm PO4 |  | (µS/cm) | (ppm SiO2) | ppm PO4 |  | (µS/cm) | (ppm SiO2) | ppm PO4 |  | (µS/cm) | (ppm SiO2) | ppm PO4 |  | (µS/cm) | (ppm SiO2) | ppm PO4 |  | (µS/cm) | (ppm SiO2) | ppm PO4 |  | (µS/cm) | (ppm SiO2) | ppm PO4 |  | (µS/cm) | (ppm) | (ppm) | (ppm) | (ppm SiO2) | ppm PO4 | (ppm sulphite) |  | (µS/cm) | (ppm) | (ppm) | (ppm) | (ppm SiO2) | ppm PO4 | (ppm sulphite) |  | (µS/cm) | (ppm) | (ppm) | (ppm) | (ppm SiO2) | ppm PO4 | (ppm sulphite) |  | (µS/cm) | (ppm) | (ppm) | (ppm) | (ppm SiO2) | ppm PO4 | (ppm sulphite) |  | (µS/cm) | (ppm) | (ppm) | (ppm) | (ppm SiO2) | ppm PO4 | (ppm sulphite) |  | (µS/cm) | (ppm) | (ppm) | (ppm) | (ppm SiO2) | ppm PO4 | (ppm sulphite) |  | (µS/cm) | (ppm SiO2) |  | (µS/cm) |  | (µS/cm) |  | (µS/cm) |  | (µS/cm) |  | (µS/cm)
| 5.5 - 7.0 | < 25.0 | 0.1; Max | 0.16 ; Max | 0.05 ; Max |  | 8.0 - 9.2 | 10.00; Max | 1.50 ; Max | 0.30 ; Max | 5 ; Max | 8.8 - 9.3 | 25 ; Max | 0.05 ; Max | 0.1; Max | N/A | 0.8-1.2 | 15 ; Max | 8.8 - 9.3 | 25 ; Max | 0.05 ; Max | 0.1; Max | N/A | 0.8-1.2 | 15 ; Max | 8.8 - 9.3 | 25 ; Max | 0.05 ; Max | 0.1; Max | N/A | 0.8-1.2 | 15 ; Max | 8.8 - 9.6 | 25 ; Max | 0.05 ; Max | 0.1; Max | N/A | 0.8-1.2 | 15 ; Max | 8.8 - 9.6 | 25 ; Max | 0.05 ; Max | 0.1; Max | 5 ; Max | 0.8-1.2 | 15 ; Max | 8.8 - 9.6 | 25 ; Max | 0.05 ; Max | 0.1; Max | 5 ; Max | 0.8-1.2 | 15 ; Max | 8.3 - 10.5 | 110 ; Max | 0.3 ; Max | 1.5; Max | 5 ; Max | 15 ; Max | 8.3 - 10.5 | 110 ; Max | 0.3 ; Max | 1.5; Max | 5 ; Max | 15 ; Max | 8.3 - 10.5 | 110 ; Max | 0.3 ; Max | 1.5; Max | 5 ; Max | 15 ; Max | 8.3 - 10.5 | 110 ; Max | 0.3 ; Max | 1.5; Max | 5 ; Max | 15 ; Max | 8.3 - 10.5 | 110 ; Max | 0.3 ; Max | 1.5; Max | 5 ; Max | 15 ; Max | 9.0 - 11.0 | 500 ; Max | 15 ; Max | 5.0 - 15.0 | 9.0 - 11.0 | 500 ; Max | 15 ; Max | 5.0 - 15.0 | 9.0 - 11.0 | 500 ; Max | 15 ; Max | 5.0 - 15.0 | 9.0 - 11.0 | 500 ; Max | 15 ; Max | 5.0 - 15.0 | 9.0 - 11.0 | 3200 ; Max | 8 ; Max | 5.0 - 15.0 | 9.0 - 11.0 | 3200 ; Max | 8 ; Max | 5.0 - 15.0 | 9.0 - 11.0 | 3200 ; Max | 8 ; Max | 5.0 - 15.0 | 10.0 - 12.0 | 4800 ; Max | 700 ; Max | 500 ; Max | 300 ; Max | 150; Max | 10 - 30 | 10 - 30 | 10.0 - 12.0 | 4800 ; Max | 700 ; Max | 500 ; Max | 300 ; Max | 150; Max | 10 - 30 | 10 - 30 | 10.0 - 12.0 | 4800 ; Max | 700 ; Max | 500 ; Max | 300 ; Max | 150; Max | 10 - 30 | 10 - 30 | 10.0 - 12.0 | 4800 ; Max | 700 ; Max | 500 ; Max | 300 ; Max | 150; Max | 10 - 30 | 10 - 30 | 10.0 - 12.0 | 4800 ; Max | 700 ; Max | 500 ; Max | 300 ; Max | 150; Max | 10 - 30 | 10 - 30 | 10.0 - 12.0 | 4800 ; Max | 700 ; Max | 500 ; Max | 300 ; Max | 150; Max | 10 - 30 | 10 - 30 | 8.5 - 9.0 | < 8.0 | 0.05 ; Max | 8.0 - 9.2 | < 10.0 | 8.0 - 9.2 | < 10.0 | 8.0 - 9.2 | < 10.0 | 8.5 - 9.0 | < 8.0 | 8.0 - 9.2 | < 10.0
2026-09-01 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 0% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | stop | stop | stop | no data | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop
2026-09-02 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop
2026-09-03 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop
2026-09-04 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop
2026-09-05 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop
2026-09-06 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | 100% | 0% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 0% | 100% | 0% | 100% | 100% | stop | stop | stop | stop
2026-09-07 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop
2026-09-08 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop
2026-09-09 | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 0% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop
2026-09-10 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop
2026-09-11 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop
2026-09-12 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop
2026-09-13 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | stop | stop | stop | stop
2026-09-14 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop
2026-09-15 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop
2026-09-16 | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | stop | stop | stop | stop
2026-09-17 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | 100% | stop | stop | stop | stop
2026-09-18 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop
2026-09-19 | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop
2026-09-20 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 0% | 100% | no data | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 0% | 100% | no data | 100% | 100% |  | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop
2026-09-21 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 0% | 100% | no data | 100% | 100% | no data | 0% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 0% | 100% | no data | 100% | 100% | no data | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | stop | stop | stop | stop
2026-09-22 | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop
2026-09-23 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | stop | stop | stop | stop | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop
2026-09-24 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop
2026-09-25 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop
2026-09-26 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 0% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 0% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop
2026-09-27 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | stop | stop | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop
2026-09-28 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | stop | stop | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 0% | 100% | stop | stop | stop | stop | stop | stop
2026-09-29 | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | stop | stop | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop
2026-09-30 | no data | no data | no data | no data | no data | no data | 0% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | stop | stop | no data | 100% | 100% | 100% | 100% | 100% | no data | stop | stop | stop | stop | stop | no data | stop | stop | no data | stop | stop | no data | 100% | 100% | no data | 100% | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop
2026-10-01 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
CONFORMANCE | 100% | 100% | 100% | 100% | 100% | 100% | 80% | 100% | 100% | 100% |  | 93.33% | 96.67% | 96.67% | 100% | 100% | 93.33% | 100% | 93.33% | 96.67% | 100% | 100% | 100% | 86.67% | 0% | 96.67% | 100% | 100% | 100% | 100% | 90% |  | 83.33% | 90% | 100% | 100% | 100% |  | 100% | [14 empty] | 88.46% | 100% | 100% |  | 100% |  | 96.67% | 100% | 100% |  | 100% | [13 empty] | 90% | 100% | 100% |  | 100% |  | 100% | 93.75% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 96% | 100% | 100% | 100% | 100% | 100% | 100% | 96.67% | [8 empty] | 100% | 100% |  |  | 100% | 100% | 77.27% | 90.91% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 96.15% | 100% | [16 empty] | 100% | 100% | 100% | 100% | 96.67% | 100% | 100% | 93.33% | 81.48% | 96.3% | 100% | 96.67% | 93.33% | 96.67% | 96.67% | 91.3% | 95.65%
overall value | [95 empty] | 0%
Date | DEMIN TANK | CONDENSATE TANK 200 | BFW PP | BFW HP COAL | BFW HP GAS |  | BFW MP | BFW TOH | BFW HRSG | BFW OMNICAL | BOILER PP #1 | BOILER PP #2 | BOILER PP #3 | BOILER PP #4 | BOILER CFBC | BOILER HP COAL | BOILER HP GAS | BOILER MP | BOILER TOH #3 | BOILER TOH #3 | BOILER TOH #4 | BOILER HRSG #1 | BOILER HRSG #2 | OMNICAL | CONDENSATE TURBIN #3 | CONDENSATE MPS PP | CONDENSATE MPS PP | CONDENSATE LPS PP | CONDENSATE MPS BH | CONDENSATE HPS BH | CONDENSATE MPS GT
2026-09-01 | 100% | 100% | 85.71% | stop | stop |  | 100% | 100% | stop | 100% | 100% | stop | stop | 100% | 100% | stop | stop | 100% | 100% | 100% | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop
2026-09-02 | 100% | 100% | 96.43% | stop | stop |  | 100% | 100% | stop | 100% | 100% | stop | stop | 75% | 100% | stop | stop | 100% | 100% | 100% | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop
2026-09-03 | 100% | 100% | 96.43% | stop | stop |  | 100% | 100% | stop | 100% | 100% | stop | stop | 100% | 100% | stop | stop | 100% | 100% | 100% | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop
2026-09-04 | 100% | 100% | 92.86% | stop | stop |  | 100% | 100% | stop | 100% | 100% | stop | 100% | 100% | 100% | stop | stop | 100% | 100% | 100% | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop
2026-09-05 | 100% | 100% | 92.86% | stop | stop |  | 100% | 100% | stop | 100% | 100% | stop | 100% | stop | 100% | stop | stop | 87.5% | 100% | 100% | 100% | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop
2026-09-06 | 100% | 100% | 78.57% | stop | stop |  | 100% | 100% | stop | 100% | 75% | stop | 100% | stop | 100% | stop | stop | 100% | 100% | 100% | 100% | stop | stop | 100% | 66.67% | 100% | 50% | 50% | 100% | stop | stop
2026-09-07 | 100% | 100% | 82.14% | stop | stop |  | 100% | 100% | stop | 100% | 100% | stop | 100% | stop | 100% | stop | stop | 87.5% | 100% | 100% | 100% | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop
2026-09-08 | 100% | 100% | 96.43% | stop | stop |  | 100% | 100% | stop | 100% | 100% | stop | 100% | stop | 100% | stop | stop | 87.5% | 100% | 100% | 100% | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop
2026-09-09 | 100% | 75% | 92.86% | stop | stop |  | 100% | 100% | stop | 100% | 100% | stop | 100% | stop | 75% | stop | stop | 87.5% | 100% | 100% | 100% | stop | stop | 87.5% | 100% | 100% | 100% | 100% | 100% | stop | stop
2026-09-10 | 100% | 100% | 96.43% | stop | stop |  | 100% | 100% | stop | 100% | stop | stop | 100% | 100% | 100% | stop | stop | 100% | stop | stop | 100% | stop | stop | 100% | stop | stop | 100% | 100% | 100% | stop | stop
2026-09-11 | 100% | 100% | 92.86% | stop | stop |  | 100% | 100% | stop | 100% | stop | stop | 100% | 100% | 100% | stop | stop | 100% | stop | stop | 100% | stop | stop | 100% | stop | stop | 100% | 100% | 100% | stop | stop
2026-09-12 | 100% | 100% | 89.29% | stop | stop |  | 100% | 100% | stop | 100% | stop | stop | 100% | 100% | 100% | stop | stop | 100% | stop | stop | 100% | stop | stop | 100% | stop | stop | 100% | 100% | 100% | stop | stop
2026-09-13 | 100% | 100% | 96.43% | stop | stop |  | 100% | 100% | stop | 100% | stop | stop | 100% | 100% | 100% | stop | stop | 100% | stop | stop | 100% | stop | stop | 100% | 100% | 100% | 50% | 100% | 100% | stop | stop
2026-09-14 | 100% | 100% | 96.43% | stop | stop |  | 100% | 100% | stop | 100% | stop | stop | 100% | 100% | 100% | stop | stop | 100% | stop | stop | 100% | stop | stop | 100% | 66.67% | 100% | 100% | 100% | 100% | stop | stop
2026-09-15 | 100% | 100% | 96.43% | stop | stop |  | 100% | 100% | stop | 100% | stop | stop | 100% | 100% | 100% | stop | stop | 100% | stop | stop | 100% | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop
2026-09-16 | 100% | 75% | 100% | stop | stop |  | 100% | 100% | stop | 100% | stop | 100% | stop | 100% | 100% | stop | stop | 100% | stop | stop | 100% | stop | stop | 87.5% | 66.67% | 100% | 100% | 100% | 50% | stop | stop
2026-09-17 | 100% | 100% | 96.43% | stop | stop |  | 100% | 100% | stop | 100% | stop | 100% | stop | 100% | 100% | stop | stop | 100% | stop | stop | 100% | stop | stop | 87.5% | 66.67% | 50% | 50% | 100% | 50% | stop | stop
2026-09-18 | 100% | 100% | 100% | stop | stop |  | 100% | 100% | stop | 100% | stop | 100% | stop | 100% | 100% | stop | stop | 100% | stop | stop | 100% | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop
2026-09-19 | 100% | 75% | 96.43% | stop | stop |  | 100% | 100% | stop | 100% | stop | 100% | stop | 100% | 100% | stop | stop | 87.5% | stop | stop | 87.5% | stop | stop | 100% | 66.67% | 100% | 100% | 100% | 100% | stop | stop
2026-09-20 | 100% | 100% | 96.43% | stop | stop |  | 75% | 100% | stop | 75% | stop | 100% | stop | 100% | 100% | stop | stop | 100% | stop | stop | 100% | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop
2026-09-21 | 100% | 100% | 96.43% | stop | stop |  | 75% | 80% | stop | 75% | stop | 100% | stop | 100% | 100% | stop | stop | 75% | stop | stop | 100% | stop | stop | 100% | 100% | 100% | 100% | 100% | 50% | stop | stop
2026-09-22 | 100% | 75% | 92.86% | stop | stop |  | 100% | 100% | stop | 100% | stop | 100% | stop | 100% | 100% | stop | stop | 100% | stop | stop | 100% | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop
2026-09-23 | 100% | 100% | 89.29% | stop | stop |  | 100% | 100% | stop | 100% | stop | 100% | stop | 100% | 100% | stop | stop | stop | stop | stop | 100% | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop
2026-09-24 | 100% | 100% | 96.43% | stop | stop |  | 100% | 100% | stop | 100% | 100% | 100% | stop | 100% | 100% | stop | stop | stop | stop | stop | 100% | stop | stop | 100% | 100% | 100% | 100% | 100% | stop | stop | stop
2026-09-25 | 100% | 100% | 96.43% | stop | stop |  | 100% | 100% | stop | 100% | 100% | 100% | stop | 100% | 100% | stop | stop | stop | stop | stop | 100% | stop | stop | 100% | 100% | 100% | 100% | 100% | stop | stop | stop
2026-09-26 | 100% | 100% | 82.14% | stop | stop |  | 75% | 100% | stop | 75% | 100% | 100% | stop | 100% | 100% | stop | stop | stop | stop | stop | 100% | stop | stop | 100% | 100% | 100% | 100% | 100% | stop | stop | stop
2026-09-27 | 100% | 100% | 96.43% | stop | stop |  | stop | 100% | stop | 100% | 100% | 100% | stop | 100% | 100% | stop | stop | stop | stop | stop | 100% | stop | stop | 100% | 100% | 100% | 100% | 100% | stop | stop | stop
2026-09-28 | 100% | 100% | 96.43% | stop | stop |  | stop | 100% | stop | 100% | 100% | 100% | stop | 100% | 100% | stop | stop | stop | stop | stop | 100% | stop | stop | 100% | 66.67% | 100% | 100% | 50% | stop | stop | stop
2026-09-29 | 100% | 75% | 96.43% | stop | stop |  | stop | 100% | stop | 100% | 100% | 100% | stop | 100% | 100% | stop | stop | stop | stop | stop | 100% | stop | stop | 100% | 100% | 100% | 100% | 100% | stop | stop | stop
2026-09-30 | no data | 75% | 92.86% | stop | stop |  | stop | 100% | stop | 100% | 100% | 100% | stop | 100% | 100% | stop | stop | stop | stop | stop | 100% | stop | stop | 100% | 100% | 100% | 100% | 100% | stop | stop | stop
2026-10-01 | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
conformance | 100% | 95% | 93.57% |  |  |  | 97.12% | 99.33% |  | 97.5% | 98.44% | 100% | 100% | 99% | 99.17% |  |  | 96.02% | 100% | 100% | 99.52% |  |  | 98.75% | 92.59% | 98.15% | 95% | 96.67% | 93.48%
BOILER & BFW
2026-09-01 | 99.21%
2026-09-02 | 98.41%
2026-09-03 | 99.8%
2026-09-04 | 99.62%
2026-09-05 | 98.97%
2026-09-06 | 90.54%
2026-09-07 | 98.4%
2026-09-08 | 99.15%
2026-09-09 | 95.68%
2026-09-10 | 99.76%
2026-09-11 | 99.52%
2026-09-12 | 99.29%
2026-09-13 | 96.85%
2026-09-14 | 97.83%
2026-09-15 | 99.79%
2026-09-16 | 92.89%
2026-09-17 | 88.27%
2026-09-18 | 100%
2026-09-19 | 94.89%
2026-09-20 | 96.85%
2026-09-21 | 91.26%
2026-09-22 | 98.11%
2026-09-23 | 99.33%
2026-09-24 | 99.78%
2026-09-25 | 99.78%
2026-09-26 | 95.76%
2026-09-27 | 99.76%
2026-09-28 | 94.21%
2026-09-29 | 98.1%
2026-09-30 | 97.7%
2026-10-01
Note on AH5: Tgl 5 March 2026, feed boiler CFBC mix condensat return & demin

## CHEMICAL CONSUMPT BOILER (hidden)
DEAERATOR & BOILER
| POWER PLANT | [27 empty] | BOILER HP | [15 empty] | BOILER HRSG TOH | [15 empty] | BOILER HRSG GAS TURBIN | [15 empty] | BOILER OMNICAL & MP
DATE | DEAERATOR |  |  |  | BOILER PP#1 | [5 empty] | BOILER PP#2 | [5 empty] | BOILER PP#3 | [5 empty] | BOILER PP#4 | [5 empty] | BOILER HP GAS | [7 empty] | BOILER HP COAL | [7 empty] | BOILER TOH #3 | [7 empty] | BOILER TOH #4 | [7 empty] | BOILER HRSG GT #1 | [7 empty] | BOILER HRSG GT #2 | [7 empty] | BOILER OMNICAL | [7 empty] | BOILER MP
| N-1700 (DEA#1,2) |  | N-1700 (DEA#3) |  | N-7208 |  | N-2556 |  | N-2584 |  | N-7208 |  | N-2556 |  | N-2584 |  | N-7208 |  | N-2556 |  | N-2584 |  | N-7208 |  | N-2556 |  | N-2584 |  | N-1700 |  | N-7208 |  | N-2556 |  | N-2584 |  | N-1700 |  | N-7208 |  | N-2556 |  | N-2584 |  | N-2811 |  | N-3273 |  | N-2556 |  | N-2584 |  | N-2811 |  | N-3273 |  | N-2556 |  | N-2584 |  | N-2811 |  | N-3273 |  | N-2556 |  | N-2584 |  | N-2811 |  | N-3273 |  | N-2556 |  | N-2584 |  | N-2811 |  | N-3273 |  | N-2556 |  | N-2584 |  | N-2811 |  | N-3273 |  | N-2556 |  | N-2584
| STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam | STROKE (%) | kg/24 jam
2020-05-01
2020-05-02
2020-05-03
2020-05-04
2020-05-05
2020-05-06
2020-05-07
2020-05-08
2020-05-09
2020-05-10
2020-05-11
2020-05-12
2020-05-13
2020-05-14
2020-05-15
2020-05-16
2020-05-17
2020-05-18
2020-05-19
2020-05-20
2020-05-21
2020-05-22
2020-05-23
2020-05-24
2020-05-25
2020-05-26
2020-05-27
2020-05-28
2020-05-29
2020-05-30
2020-05-31

## LAY UP BOILER
| Boiler HP Coal |  |  |  | Boiler HP Gas |  |  |  | Boiler MP | [7 empty] | Boiler HRSG TOH #3 | [7 empty] | Boiler HRSG TOH #4 | [7 empty] | Boiler OMNICAL
Parameter | pH | Conductivity | Silica | Phosphate | pH | Conductivity | Silica | Phosphate | pH | Conductivity | P - Alkalinity | M - Alkalinity | O - Alkalinity | Silica | Phosphate | Sulphite | pH | Conductivity | P - Alkalinity | M - Alkalinity | O - Alkalinity | Silica | Phosphate | Sulphite | pH | Conductivity | P - Alkalinity | M - Alkalinity | O - Alkalinity | Silica | Phosphate | Sulphite | pH | Conductivity | P - Alkalinity | M - Alkalinity | O - Alkalinity | Silica | Phosphate | Sulphite
|  | (µS/cm) | (ppm SiO2) | ppm PO4 |  | (µS/cm) | (ppm SiO2) | ppm PO4 |  | (µS/cm) | (ppm) | (ppm) | (ppm) | (ppm SiO2) | ppm PO4 | (ppm sulphite) |  | (µS/cm) | (ppm) | (ppm) | (ppm) | (ppm SiO2) | ppm PO4 | (ppm sulphite) |  | (µS/cm) | (ppm) | (ppm) | (ppm) | (ppm SiO2) | ppm PO4 | (ppm sulphite) |  | (µS/cm) | (ppm) | (ppm) | (ppm) | (ppm SiO2) | ppm PO4 | (ppm sulphite)
| 9.0 - 11.0 | 3200 ; Max | 8 ; Max | 5.0 - 15.0 | 9.0 - 11.0 | 3200 ; Max | 8 ; Max | 5.0 - 15.0 | 10.0 - 12.0 | 4800 ; Max | 700 ; Max | 500 ; Max | 300 ; Max | 150; Max | 10 - 30 | 10 - 30 | 10.0 - 12.0 | 4800 ; Max | 700 ; Max | 500 ; Max | 300 ; Max | 150; Max | 10 - 30 | 10 - 30 | 10.0 - 12.0 | 4800 ; Max | 700 ; Max | 500 ; Max | 300 ; Max | 150; Max | 10 - 30 | 10 - 30 | 10.0 - 12.0 | 4800 ; Max | 700 ; Max | 500 ; Max | 300 ; Max | 150; Max | 10 - 30 | 10 - 30
Date
2026-09-01
2026-09-02
2026-09-03 | 9.18 | 17.68 | 1 | 3.5 | 9.08 | 9.1 | 1 | 0.6
2026-09-04
2026-09-05
2026-09-06
2026-09-07
2026-09-08
2026-09-09
2026-09-10 | 9.28 | 44.49 | 1 | 6 | 8.87 | 6.53 | 1 | 0.6
2026-09-11
2026-09-12
2026-09-13
2026-09-14
2026-09-15
2026-09-16
2026-09-17 | 8.68 | 13.01 | 1 | 1.7 | 8.78 | 8.31 | 1 | 0.2
2026-09-18
2026-09-19
2026-09-20
2026-09-21
2026-09-22
2026-09-23
2026-09-24 | 10.6 | 224.3 | 1 | 3.5 | 9.73 | 16.85 | 1 | 0.5
2026-09-25
2026-09-26
2026-09-27
2026-09-28
2026-09-29
2026-09-30
2026-10-01
| Boiler HP Coal |  |  |  | Boiler HP Gas |  |  |  | Boiler MP | [7 empty] | Boiler HRSG TOH #3 | [7 empty] | Boiler HRSG TOH #4 | [7 empty] | Boiler OMNICAL
Parameter | pH | Conductivity | Silica | Phosphate | pH | Conductivity | Silica | Phosphate | pH | Conductivity | P - Alkalinity | M - Alkalinity | O - Alkalinity | Silica | Phosphate | Sulphite | pH | Conductivity | P - Alkalinity | M - Alkalinity | O - Alkalinity | Silica | Phosphate | Sulphite | pH | Conductivity | P - Alkalinity | M - Alkalinity | O - Alkalinity | Silica | Phosphate | Sulphite | pH | Conductivity | P - Alkalinity | M - Alkalinity | O - Alkalinity | Silica | Phosphate | Sulphite
|  | (µS/cm) | (ppm SiO2) | ppm PO4 |  | (µS/cm) | (ppm SiO2) | ppm PO4 |  | (µS/cm) | (ppm) | (ppm) | (ppm) | (ppm SiO2) | ppm PO4 | (ppm sulphite) |  | (µS/cm) | (ppm) | (ppm) | (ppm) | (ppm SiO2) | ppm PO4 | (ppm sulphite) |  | (µS/cm) | (ppm) | (ppm) | (ppm) | (ppm SiO2) | ppm PO4 | (ppm sulphite) |  | (µS/cm) | (ppm) | (ppm) | (ppm) | (ppm SiO2) | ppm PO4 | (ppm sulphite)
| 9.0 - 11.0 | 3200 ; Max | 8 ; Max | 5.0 - 15.0 | 9.0 - 11.0 | 3200 ; Max | 8 ; Max | 5.0 - 15.0 | 10.0 - 12.0 | 4800 ; Max | 700 ; Max | 500 ; Max | 300 ; Max | 150; Max | 10 - 30 | 10 - 30 | 10.0 - 12.0 | 4800 ; Max | 700 ; Max | 500 ; Max | 300 ; Max | 150; Max | 10 - 30 | 10 - 30 | 10.0 - 12.0 | 4800 ; Max | 700 ; Max | 500 ; Max | 300 ; Max | 150; Max | 10 - 30 | 10 - 30 | 10.0 - 12.0 | 4800 ; Max | 700 ; Max | 500 ; Max | 300 ; Max | 150; Max | 10 - 30 | 10 - 30
2026-09-01 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-02 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-03 | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-04 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-05 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-06 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-07 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-08 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-09 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-10 | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 0% | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-11 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-12 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-13 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-14 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-15 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-16 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-17 | 0% | 100% | 100% | 0% | 0% | 100% | 100% | 0% | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-18 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-19 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-20 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-21 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-22 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-23 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-24 | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 0% | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-25 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-26 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-27 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-28 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-29 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-09-30 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2026-10-01 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
CONFORMANCE | 75% | 100% | 100% | 25% | 50% | 100% | 100% | 0%
overall value
Date
2026-09-01
2026-09-02
2026-09-03
2026-09-04
2026-09-05
2026-09-06
2026-09-07
2026-09-08
2026-09-09
2026-09-10
2026-09-11
2026-09-12
2026-09-13
2026-09-14
2026-09-15
2026-09-16
2026-09-17
2026-09-18
2026-09-19
2026-09-20
2026-09-21
2026-09-22
2026-09-23
2026-09-24
2026-09-25
2026-09-26
2026-09-27
2026-09-28
2026-09-29
2026-09-30
2026-10-01
conformance
2026-09-01
2026-09-02
2026-09-03
2026-09-04
2026-09-05
2026-09-06
2026-09-07
2026-09-08
2026-09-09
2026-09-10
2026-09-11
2026-09-12
2026-09-13
2026-09-14
2026-09-15
2026-09-16
2026-09-17
2026-09-18
2026-09-19
2026-09-20
2026-09-21
2026-09-22
2026-09-23
2026-09-24
2026-09-25
2026-09-26
2026-09-27
2026-09-28
2026-09-29
2026-09-30
2026-10-01

## COOLING TOWER
| COOLING TOWER HRSG GT#1 | [10 empty] | COOLING TOWER HRSG GT#2 | [10 empty] | COOLING TOWER POWER PLANT #1,2 | [10 empty] | COOLING TOWER POWER PLANT #3 | [10 empty] | COOLING TOWER POWER PLANT #4 | [10 empty] | COOLING TOWER COMPRESSOR | [10 empty] | COOLING TOWER COMPRESSOR #2 | [10 empty] | COOLING TOWER BOILER HOUSE
| MAKE UP CT |  | COOLING TOWER | [8 empty] | MAKE UP CT |  | COOLING TOWER | [8 empty] | MAKE UP CT |  | COOLING TOWER | [8 empty] | MAKE UP CT |  | COOLING TOWER | [8 empty] | MAKE UP CT |  | COOLING TOWER | [8 empty] | MAKE UP CT |  | COOLING TOWER | [8 empty] | MAKE UP CT |  | COOLING TOWER | [8 empty] | MAKE UP CT |  | COOLING TOWER
DATE | pH | Conductivity | pH | Conductivity | Ca-Hardness | Iron | Silica | Orthophosphate (filter) | Free Chlorine | Chloride | Turbidity | pH | Conductivity | pH | Conductivity | Ca-Hardness | Iron | Silica | Orthophosphate (filter) | Free Chlorine | Chloride | Turbidity | pH | Conductivity | pH | Conductivity | Ca-Hardness | Iron | Silica | Orthophosphate (filter) | Free Chlorine | Chloride | Turbidity | pH | Conductivity | pH | Conductivity | Ca-Hardness | Iron | Silica | Orthophosphate (filter) | Free Chlorine | Chloride | Turbidity | pH | Conductivity | pH | Conductivity | Ca-Hardness | Iron | Silica | Orthophosphate (filter) | Free Chlorine | Chloride | Turbidity | pH | Conductivity | pH | Conductivity | Ca-Hardness | Iron | Silica | Orthophosphate (filter) | Free Chlorine | Chloride | Turbidity | pH | Conductivity | pH | Conductivity | Ca-Hardness | Iron | Silica | Orthophosphate (filter) | Free Chlorine | Chloride | Turbidity | pH | Conductivity | pH | Conductivity | Ca-Hardness | Iron | Silica | Chloride | Turbidity
|  | (µS/cm) |  | (µS/cm) | ppm CaCO3 | ppm Fe | ppm SiO2 | ppm PO4 | ppm Cl2 | ppm Cl- | NTU |  | (µS/cm) |  | (µS/cm) | ppm CaCO3 | ppm Fe | ppm SiO2 | ppm PO4 | ppm Cl2 | ppm Cl- | NTU |  | (µS/cm) |  | (µS/cm) | ppm CaCO3 | ppm Fe | ppm SiO2 | ppm PO4 | ppm Cl2 | ppm Cl- | NTU |  | (µS/cm) |  | (µS/cm) | ppm CaCO3 | ppm Fe | ppm SiO2 | ppm PO4 | ppm Cl2 | ppm Cl- | NTU |  | (µS/cm) |  | (µS/cm) | ppm CaCO3 | ppm Fe | ppm SiO2 | ppm PO4 | ppm Cl2 | ppm Cl- | NTU |  | (µS/cm) |  | (µS/cm) | ppm CaCO3 | ppm Fe | ppm SiO2 | ppm PO4 | ppm Cl2 | ppm Cl- | NTU |  | (µS/cm) |  | (µS/cm) | ppm CaCO3 | ppm Fe | ppm SiO2 | ppm PO4 | ppm Cl2 | ppm Cl- | NTU |  | (µS/cm) |  | (µS/cm) | ppm CaCO3 | ppm Fe | ppm SiO2 | ppm Cl- | NTU
| 5.5 - 7.0 | < 50 | 7.0 - 9.0 | 700; max | 200; max | 2,max | 150; max | 6.0 - 12.0 | 0.2 - 0.5 | 150,max | 20,max | 5.5 - 7.0 | < 50 | 7.0 - 9.0 | 700; max | 200; max | 2,max | 150; max | 6.0 - 12.0 | 0.2 - 0.5 | 150,max | 20,max | 5.5 - 7.0 | < 50 | 7.0 - 9.0 | 700; max | 200; max | 2,max | 150; max | 6.0 - 12.0 | 0.2 - 0.5 | 150,max | 20,max | 5.5 - 7.0 | < 50 | 7.0 - 9.0 | 700; max | 200; max | 2,max | 150; max | 6.0 - 12.0 | 0.2 - 0.5 | 150,max | 20,max | 5.5 - 7.0 | < 50 | 7.0 - 9.0 | 1000; max | 200; max | 2,max | 150; max | 6.0 - 12.0 | 0.2 - 0.5 | 200,max | 20,max | 5.5 - 7.0 | < 50 | 7.0 - 9.0 | 700; max | 200; max | 2,max | 150; max | 6.0 - 12.0 | 0.2 - 0.5 | 150,max | 20,max | 5.5 - 7.0 | < 50 | 7.0 - 9.0 | 700; max | 200; max | 2,max | 150; max | 6.0 - 12.0 | 0.2 - 0.5 | 150,max | 20,max | 5.5 - 7.0 | < 50 | 7.0 - 9.0 | 700; max | 200; max | 2,max | 150; max | 150,max | 20,max
2026-09-01 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 5.92 | 50 | 8.36 | 975.7 |  | 1.22 |  |  | 0.46 | 189.68 | 11.4 | 5.65 | 37.26 | 8.3 | 598.1 |  | 0.86 |  |  | 0.5 | 126.73 | 2.47 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-02 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 5.933 | 41.38 | 8.39 | 967 |  | 1.68 |  | 9.75 | 0.48 | 197.79 | 10.2 | 5.82 | 43.48 | 8.77 | 472.4 |  | 0.24 |  | 7.45 | 0.39 | 73.85 | 3.48 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-03 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 5.86 | 33.73 | 8.62 | 904.6 |  | 1.51 |  |  | 0.24 | 185.43 | 8.31 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-04 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.05 | 35.97 | 8.57 | 850.6 | 8 | 1.28 | 4 | 7.2 | 0.28 | 167.4 | 7.61 | 6 | 39.09 | 8.76 | 459.7 | 2 | 0.48 | 4 | 9.05 | 0.43 | 79.13 | 4 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-05 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6 | 42.86 | 8.34 | 886.3 |  | 1.7 |  |  | 0.5 | 171.82 | 6.86 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 5.56 | 36.29 | 7.81 | 365.1 | 2 | 0.01 | 2 | 54.74 | 1.86
2026-09-06
2026-09-07 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.13 | 42.73 | 8.57 | 844.1 |  | 1.28 |  | 10.45 | 0.22 | 186.08 | 7.86 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-08 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 5.72 | 39.22 | 8.05 | 813.7 |  | 0.91 |  |  | 0.2 | 174.29 | 7.58 | 5.9 | 32.38 | 8.44 | 405.8 |  | 0.74 |  |  | 0.2 | 50.48 | 3.71 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-09 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 5.86 | 34.24 | 7.74 | 764.3 |  | 1.29 |  | 11.05 | 0.21 | 170.99 | 5.97 | 5.83 | 29.8 | 7.7 | 457 |  | 1.79 |  | 7.4 | 0.21 | 92.93 | 11.5 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-10 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 5.7 | 27.81 | 8.14 | 656.9 |  | 1.16 |  |  | 0.2 | 150.4 | 5.38 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-11 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 5.81 | 29.4 | 8.1 | 654.3 | 4 | 1.19 | 2 | 10.65 | 0.31 | 155.81 | 5.51 | 5.87 | 30.71 | 7.94 | 588.7 | 8 | 1.28 | 8 | 10.4 | 0.2 | 128.23 | 9.51 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-12 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 5.83 | 30.52 | 8.29 | 586 |  | 0.97 |  |  | 0.24 | 128.22 | 5.59 | 5.74 | 28.07 | 7.96 | 554.8 |  | 0.78 |  |  | 0.2 | 116.43 | 3.27 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 5.9 | 43.43 | 7.78 | 287 | 6 | 0.04 | 4 | 45.25 | 0.51
2026-09-13 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-14 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 5.67 | 29.02 | 8.26 | 678.6 |  | 1.2 |  | 10.05 | 0.24 | 155.64 | 8.32 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-15 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 5.86 | 44.76 | 8.54 | 895.4 |  | 1.25 |  |  | 0.21 | 173.47 | 10.6 | 5.51 | 43.5 | 8.43 | 634.1 |  | 0.74 |  |  | 0.27 | 124.78 | 1.36 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-16 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 5.78 | 38.47 | 8.16 | 910.2 |  | 1.35 |  | 11.8 | 0.2 | 182.07 | 10.7 | 5.57 | 57.9 | 8.27 | 560.1 |  | 0.55 |  | 8.25 | 0.4 | 113.54 | 8.05 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-17 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 5.93 | 49.73 | 8.1 | 920.3 |  | 1.32 |  |  | 0.36 | 178.2 | 11.7 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-18 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 5.88 | 47.32 | 8.55 | 883.3 | 4 | 1.3 | 5 | 10.6 | 0.23 | 180.22 | 12.1 | 5.53 | 44.87 | 8 | 548 | 4 | 0.5 | 9 | 10.75 | 0.26 | 94.88 | 1.54 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-19 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 5.95 | 38.07 | 8.83 | 789.9 |  | 1.24 |  |  | 0.44 | 164.67 | 9.39 | 5.6 | 44.67 | 8.28 | 512.4 |  | 0.51 |  |  | 0.47 | 97.14 | 1.66 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 5.83 | 43.89 | 7.96 | 306.4 | 6 | 0.05 | 4 | 49.94 | 1.29
2026-09-20
2026-09-21 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.3 | 49.57 | 7.52 | 587.8 |  | 0.94 |  | 7.2 | 0.49 | 114.17 | 8.35 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-22 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 5.87 | 54.03 | 8.57 | 533.4 |  | 0.87 |  |  | 0.44 | 106.72 | 8.5 | 5.88 | 50.39 | 8.16 | 442.5 |  | 0.54 |  |  | 0.5 | 86.75 | 4.57 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-23 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.3 | 58.75 | 8.49 | 627.4 |  | 1.12 |  | 9.55 | 0.2 | 116.34 | 8.66 | 6.2 | 58.7 | 8.6 | 722.4 |  | 0.92 |  | 6.7 | 0.47 | 143.46 | 7.59 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-24 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 5.83 | 41.48 | 8.26 | 523.7 |  | 1.2 |  |  | 0.33 | 115.48 | 8.66 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-25 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 5.98 | 40.34 | 8.29 | 552.5 | 4 | 0.94 | 2 | 6.8 | 0.5 | 124.82 | 9.12 | 5.99 | 41.55 | 7.82 | 442.2 | 4 | 0.6 | 6 | 6 | 0.5 | 88.61 | 2.78 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-26 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6 | 28 | 7.14 | 584.1 |  | 1.25 |  |  | 0.5 | 133.35 | 9.28 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 5.78 | 31.42 | 7.19 | 300.6 | 4 | 0.06 | 2 | 50.03 | 0.9
2026-09-27
2026-09-28 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 6.08 | 26.06 | 8.62 | 714.9 |  | 1.36 |  | 12 | 0.41 | 151.75 | 7.38 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-29 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 5.98 | 35.64 | 8.64 | 798.9 |  | 1.41 |  |  | 0.5 | 164.22 | 6.87 | 5.76 | 35.46 | 7.97 | 643 |  | 0.83 |  |  | 0.3 | 139.94 | 5.65 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-30 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 5.79 | 33.85 | 8.3 | 305.5 |  | 0.7 |  | 10.8 | 0.47 | 59.87 | 10.5 | 5.74 | 37.26 | 8.3 | 556.3 |  | 0.55 |  | 6.25 | 0.5 | 116.85 | 6.52 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-10-01
Consumption Chemicals HRSG #1 |  |  |  |  | Consumption Chemicals HRSG #2 |  |  | Consumption Chemicals CT. PP |  | Consumption Chemicals CT. COMPRESSOR
Stroke Dosing Pump (%) | 3DT-129 | 3DT-120 | N-3935 | N- 8507 | 3DT-129 | 3DT-120 | N-3935 | 3DT-129 | 3DT-120 | 3DT-129 | 3DT-120 | N- 8507
| SLUGDOSE | SLUGDOSE | SLUGDOSE | SLUGDOSE | SLUGDOSE | SLUGDOSE | SLUGDOSE | SLUGDOSE | SLUGDOSE | SLUGDOSE | SLUGDOSE | SLUGDOSE
DATE
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
COOLING TOWER HRSG GT#1 | [11 empty] | COOLING TOWER HRSG GT#2 | [10 empty] | COOLING TOWER POWER PLANT #1 | [10 empty] | COOLING TOWER POWER PLANT #3 | [10 empty] | COOLING TOWER POWER PLANT #4 | [10 empty] | COOLING TOWER COMPRESSOR | [10 empty] | COOLING TOWER COMPRESSOR | [10 empty] | COOLING TOWER BOILER HOUSE
MAKE UP CT |  |  | COOLING TOWER | [8 empty] | MAKE UP CT |  | COOLING TOWER | [8 empty] | MAKE UP CT |  | COOLING TOWER | [8 empty] | MAKE UP CT |  | COOLING TOWER | [8 empty] | MAKE UP CT |  | COOLING TOWER | [8 empty] | MAKE UP CT |  | COOLING TOWER | [8 empty] | MAKE UP CT |  | COOLING TOWER | [8 empty] | MAKE UP CT |  | COOLING TOWER
DATE | pH | Conductivity | pH | Conductivity | Ca-Hardness | Iron | Silica | Orthophosphate (filter) | Free Chlorine | Chloride | Turbidity | pH | Conductivity | pH | Conductivity | Ca-Hardness | Iron | Silica | Orthophosphate (filter) | Free Chlorine | Chloride | Turbidity | pH | Conductivity | pH | Conductivity | Ca-Hardness | Iron | Silica | Orthophosphate (filter) | Free Chlorine | Chloride | Turbidity | pH | Conductivity | pH | Conductivity | Ca-Hardness | Iron | Silica | Orthophosphate (filter) | Free Chlorine | Chloride | Turbidity | pH | Conductivity | pH | Conductivity | Ca-Hardness | Iron | Silica | Orthophosphate (filter) | Free Chlorine | Chloride | Turbidity | pH | Conductivity | pH | Conductivity | Ca-Hardness | Iron | Silica | Orthophosphate (filter) | Free Chlorine | Chloride | Turbidity | pH | Conductivity | pH | Conductivity | Ca-Hardness | Iron | Silica | Orthophosphate (filter) | Free Chlorine | Chloride | Turbidity | pH | Conductivity | pH | Conductivity | Ca-Hardness | Iron | Silica | Chloride | Turbidity
|  | (µS/cm) |  | (µS/cm) | ppm CaCO3 | ppm Fe | ppm SiO2 | ppm PO4 | ppm Cl2 | ppm Cl- | NTU |  | (µS/cm) |  | (µS/cm) | ppm CaCO3 | ppm Fe | ppm SiO2 | ppm PO4 | ppm Cl2 | ppm Cl- | NTU |  | (µS/cm) |  | (µS/cm) | ppm CaCO3 | ppm Fe | ppm SiO2 | ppm PO4 | ppm Cl2 | ppm Cl- | NTU |  | (µS/cm) |  | (µS/cm) | ppm CaCO3 | ppm Fe | ppm SiO2 | ppm PO4 | ppm Cl2 | ppm Cl- | NTU |  | (µS/cm) |  | (µS/cm) | ppm CaCO3 | ppm Fe | ppm SiO2 | ppm PO4 | ppm Cl2 | ppm Cl- | NTU |  | (µS/cm) |  | (µS/cm) | ppm CaCO3 | ppm Fe | ppm SiO2 | ppm PO4 | ppm Cl2 | ppm Cl- | NTU |  | (µS/cm) |  | (µS/cm) | ppm CaCO3 | ppm Fe | ppm SiO2 | ppm PO4 | ppm Cl2 | ppm Cl- | NTU |  | (µS/cm) |  | (µS/cm) | ppm CaCO3 | ppm Fe | ppm SiO2 | ppm Cl- | NTU
| 6.0 - 7.5 | < 50 | 7.0 - 9.2 | 700,max | 200; max | 2,max | 150; max | 6.0 - 12.0 | 0.2 - 0.5 | 150,max | 20,max | 6.0 - 7.5 | < 50 | 7.0 - 9.2 | 700,max | 200; max | 2,max | 150; max | 6.0 - 12.0 | 0.2 - 0.5 | 150,max | 20,max | 6.0 - 7.5 | < 50 | 7.0 - 9.2 | 700; max | 200; max | 2,max | 150; max | 6.0 - 12.0 | 0.2 - 0.5 | 150,max | 20,max | 6.0 - 7.5 | < 50 | 7.0 - 9.2 | 700; max | 200; max | 2,max | 150; max | 6.0 - 12.0 | 0.2 - 0.5 | 150,max | 20,max | 6.0 - 7.5 | < 50 | 7.0 - 9.2 | 1000,max | 200; max | 2,max | 150; max | 6.0 - 12.0 | 0.2 - 0.5 | 200,max | 20,max | 6.0 - 7.5 | < 50 | 7.0 - 9.2 | 700,max | 200; max | 2,max | 150; max | 6.0 - 12.0 | 0.2 - 0.5 | 150,max | 20,max | 6.0 - 7.5 | < 50 | 7.0 - 9.2 | 700,max | 200; max | 2,max | 150; max | 6.0 - 12.0 | 0.2 - 0.5 | 150,max | 20,max | 6.0 - 7.5 | < 50 | 7.0 - 9.2 | 700,max | 200; max | 2,max | 150; max | 150,max | 20,max
2023-01-01 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | no data | 100% | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | no data | no data | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-02 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | no data | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | no data | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-03 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | no data | 100% | no data | no data | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-04 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-05 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | no data | 100% | no data | no data | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
2023-01-06 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-07 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | no data | 100% | no data | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-08 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | no data | 100% | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | no data | no data | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-09 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | no data | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | no data | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-10 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | no data | 100% | no data | no data | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-11 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-12 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | no data | 100% | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | no data | no data | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
2023-01-13 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-14 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | no data | 100% | no data | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-15 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | no data | 100% | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | no data | no data | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-16 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | no data | 100% | no data | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | no data | 100% | no data | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-17 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | no data | 100% | no data | no data | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-18 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-19 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | no data | 100% | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | no data | no data | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
2023-01-20 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-21 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | no data | 100% | no data | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-22 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 0% | 100% | 100% | no data | 100% | no data | no data | 100% | 100% | 100% | 100% | 0% | 100% | 100% | no data | 100% | no data | no data | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-23 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 0% | 100% | 100% | no data | 100% | no data | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 0% | no data | 100% | no data | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-24 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | no data | 100% | no data | no data | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-25 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-26 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | no data | 100% | no data | no data | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
2023-01-27 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-28 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | no data | 100% | no data | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-29 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | no data | 100% | no data | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | no data | no data | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-30 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | 100% | 100% | 100% | 100% | no data | 100% | no data | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | no data | 100% | no data | 100% | 100% | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | no data | no data | no data | no data | no data | no data | no data | no data | no data
2023-01-31 | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data
CONFORMANCE | [44 empty] | 100% | 92.31% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 81.25% | 100% | 93.75% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | [11 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
OVERALL VALUE
Date | CT. HRSG #1 | CT. HRSG #2 | CT. PP | CT. COMPRESSOR | CT. BOILER HOUSE
2023-01-01 | stop | stop | 100% | 100% | no data
2023-01-02 | stop | stop | 100% | 100% | no data
2023-01-03 | stop | stop | 100% | stop | no data
2023-01-04 | stop | stop | 100% | 100% | no data
2023-01-05 | stop | stop | 100% | stop | 100%
2023-01-06 | no data | no data | no data | no data | no data
2023-01-07 | stop | stop | 100% | stop | no data
2023-01-08 | stop | stop | 100% | 100% | no data
2023-01-09 | stop | stop | 100% | 100% | no data
2023-01-10 | stop | stop | 100% | stop | no data
2023-01-11 | stop | stop | 100% | 100% | no data
2023-01-12 | stop | stop | 100% | 100% | 100%
2023-01-13 | stop | stop | no data | no data | no data
2023-01-14 | stop | stop | 100% | stop | no data
2023-01-15 | stop | stop | 100% | 100% | no data
2023-01-16 | stop | stop | 100% | 100% | no data
2023-01-17 | stop | stop | 100% | stop | no data
2023-01-18 | stop | stop | 100% | 100% | no data
2023-01-19 | stop | stop | 100% | 100% | 100%
2023-01-20 | no data | no data | no data | no data | no data
2023-01-21 | stop | stop | 100% | stop | no data
2023-01-22 | stop | stop | 87.5% | 100% | no data
2023-01-23 | stop | stop | 88.89% | 85.71% | no data
2023-01-24 | stop | stop | 100% | stop | no data
2023-01-25 | stop | stop | 100% | 100% | no data
2023-01-26 | stop | stop | 100% | stop | 100%
2023-01-27 | no data | no data | no data | no data | no data
2023-01-28 | stop | stop | 100% | stop | no data
2023-01-29 | stop | stop | 100% | 100% | no data
2023-01-30 | stop | stop | 100% | 100% | no data
2023-01-31 | no data | no data | no data | no data | no data
CONFORMANCE |  |  | 99.09% | 99.11% | 100%
COOLING TOWER
2023-01-01 | 100%
2023-01-02 | 100%
2023-01-03 | 100%
2023-01-04 | 100%
2023-01-05 | 100%
2023-01-06
2023-01-07 | 100%
2023-01-08 | 100%
2023-01-09 | 100%
2023-01-10 | 100%
2023-01-11 | 100%
2023-01-12 | 100%
2023-01-13
2023-01-14 | 100%
2023-01-15 | 100%
2023-01-16 | 100%
2023-01-17 | 100%
2023-01-18 | 100%
2023-01-19 | 100%
2023-01-20
2023-01-21 | 100%
2023-01-22 | 93.75%
2023-01-23 | 87.3%
2023-01-24 | 100%
2023-01-25 | 100%
2023-01-26 | 100%
2023-01-27
2023-01-28 | 100%
2023-01-29 | 100%
2023-01-30 | 100%
2023-01-31
Formulas:
DATE = '[2]RO & MIXBED'!A8

## Ca & Mg HARDNESS (hidden)
| Demin Tank 2000 MT |  | Deamin Tank BWRO |  | Buffer Demin |  | RO Tank 2000 |  | RO Tank 600 |  | Mixbed #2A |  | Mixbed #2B |  | Mixbed #1A |  | Mixbed #1B |  | Mixbed #3A |  | Mixbed #3B |  | Mixbed #4 |  | Mixbed #5A |  | Mixbed #5B | BFW PP#1 |  | BFW PP#2 |  | BFW PP#3 |  | BFW HP CFBC |  | BFW HP Coal |  | BFW HP Gas |  | BFW TOH |  | BFW GT#1 |  | BFW GT#2 |  | BFW OMNICHAL |  | TANK 200 |  | Dynalon #1 |  | Dynalon #2 |  | Dynalon #4 |  | Mixbed Dyn #4 |  | New RO |  | Permeate #1A |  | Permeate #1B |  | Permeate #2 |  | Permeate #3A |  | Permeate #3B |  | Permeate #4A |  | Permeate #4B
Parameter | CaCO3 | Ca | CaCO3 | Ca | Mg | Ca | Mg | Ca | Mg | Ca | CaCO3 | Ca | CaCO3 | Ca | CaCO3 | Ca | CaCO3 | Ca | CaCO3 | Ca | CaCO3 | Ca | CaCO3 | Ca | CaCO3 | Ca | CaCO3 | Mg | Ca | Mg | Ca | Mg | Ca | Mg | Ca | CaCO3 | Ca | Mg | Ca | Mg | Ca | Mg | Ca | Mg | Ca | Mg | Ca | Mg | Ca | Mg | Ca | Mg | Ca | Mg | Ca | Mg | Ca | Mg | Ca | Mg | Ca | Mg | Ca | Mg | Ca | Mg | Ca | Mg | Ca | Mg | Ca | Mg | Ca
Date
2026-09-01
2026-09-02
2026-09-03
2026-09-04
2026-09-05
2026-09-06
2026-09-07
2026-09-08
2026-09-09
2026-09-10
2026-09-11
2026-09-12
2026-09-13
2026-09-14
2026-09-15
2026-09-16
2026-09-17
2026-09-18
2026-09-19
2026-09-20
2026-09-21
2026-09-22
2026-09-23
2026-09-24
2026-09-25
2026-09-26
2026-09-27
2026-09-28
2026-09-29
2026-09-30
2026-10-01

## LAY UP CT
| COOLING TOWER HRSG GT#1 | [5 empty] | COOLING TOWER HRSG GT#2 | [5 empty] | COOLING TOWER POWER PLANT #4 |  |  |  |  | COOLING TOWER COMPRESSOR | [5 empty] | COOLING TOWER COMPRESSOR #2
| COOLING TOWER | [5 empty] | COOLING TOWER | [5 empty] | COOLING TOWER |  |  |  |  | COOLING TOWER | [5 empty] | COOLING TOWER
DATE | pH | Conductivity | Iron | Orthophosphate (filter) | Free Chlorine | Turbidity | pH | Conductivity | Iron | Orthophosphate (filter) | Free Chlorine | Turbidity | pH | Conductivity | Iron | Free Chlorine | Turbidity | pH | Conductivity | Iron | Orthophosphate (filter) | Free Chlorine | Turbidity | pH | Conductivity | Iron | Orthophosphate (filter) | Free Chlorine | Turbidity
|  | (µS/cm) | ppm Fe | ppm PO4 | ppm Cl2 | NTU |  | (µS/cm) | ppm Fe | ppm PO4 | ppm Cl2 | NTU |  | (µS/cm) | ppm Fe | ppm Cl2 | NTU |  | (µS/cm) | ppm Fe | ppm PO4 | ppm Cl2 | NTU |  | (µS/cm) | ppm Fe | ppm PO4 | ppm Cl2 | NTU
| 8.0 - 9.0 | 700; max | 2,max | 6.0, min | 1.0 - 3.0 | 20,max | 8.0 - 9.0 | 700; max | 2,max | 6.0, min | 1.0 - 3.0 | 20,max | 8.0 - 9.0 | 700; max | 2,max | 1.2 - 3.0 | 20,max | 8.0 - 9.0 | 700; max | 2,max | 6.0, min | 1.0 - 3.0 | 20,max | 8.0 - 9.0 | 700; max | 2,max | 6.0, min | 1.0 - 3.0 | 20,max
2026-09-01
2026-09-02
2026-09-03 | stop | stop | stop | stop | stop | stop | 8.43 | 374.2 | 0.9 | 7.6 | 2.2 | 4.19 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-04
2026-09-05
2026-09-06
2026-09-07 | stop | stop | stop | stop | stop | stop | 7.41 | 539.5 | 1.38 | 6 | 1.16 | 8.94 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-08
2026-09-09
2026-09-10 | stop | stop | stop | stop | stop | stop | 8.15 | 508.9 | 1.29 | 8.25 | 0.37 | 7 | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-11
2026-09-12
2026-09-13
2026-09-14 | stop | stop | stop | stop | stop | stop | 8.94 | 569.1 | 1.52 | 10.8 | 2.2 | 2.99 | [5 empty] | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-15
2026-09-16
2026-09-17 | stop | stop | stop | stop | stop | stop | 8.42 | 1033 | 0.14 | 6.2 | 2.2 | 4.7 | [5 empty] | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-18
2026-09-19
2026-09-20
2026-09-21 | stop | stop | stop | stop | stop | stop | 8.08 | 505 | 1.47 | 6.85 | 2.2 | 6.69 | [5 empty] | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-22
2026-09-23
2026-09-24 | stop | stop | stop | stop | stop | stop | 8.96 | 571.8 | 1.35 | 6.15 | 2.2 | 4.01 | [5 empty] | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-25
2026-09-26
2026-09-27
2026-09-28 | stop | stop | stop | stop | stop | stop | 8.4 | 438 | 1.16 | 8 | 2.2 | 9.12 | [5 empty] | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop | stop
2026-09-29
2026-09-30
2026-10-01
Stroke Dosing Pump (%)
DATE
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
COOLING TOWER HRSG GT#1
MAKE UP CT | 0 | [5 empty] | MAKE UP CT | [5 empty] | MAKE UP CT |  |  |  |  | MAKE UP CT | [5 empty] | MAKE UP CT
DATE | pH | Conductivity | Iron |  | Free Chlorine | Turbidity | pH | Conductivity | Iron |  | Free Chlorine | Turbidity | pH | Conductivity | Iron | Free Chlorine | Turbidity | pH | Conductivity | Iron |  | Free Chlorine | Turbidity | pH | Conductivity | Iron |  | Free Chlorine | Turbidity
|  | (µS/cm) | ppm Fe |  | ppm Cl2 | NTU |  | (µS/cm) | ppm Fe |  | ppm Cl2 | NTU |  | (µS/cm) | ppm Fe | ppm Cl2 | NTU |  | (µS/cm) | ppm Fe |  | ppm Cl2 | NTU |  | (µS/cm) | ppm Fe |  | ppm Cl2 | NTU
| 7.0 - 9.2 | 700,max | 2,max |  | 0.2 - 0.5 | 20,max | 7.0 - 9.2 | 700,max | 2,max |  | 0.2 - 0.5 | 20,max | 7.0 - 9.2 | 700,max | 2,max | 0.2 - 0.5 | 20,max | 7.0 - 9.2 | 700,max | 2,max |  | 0.2 - 0.5 | 20,max | 7.0 - 9.2 | 700,max | 2,max |  | 0.2 - 0.5 | 20,max
2023-01-01 | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data
2023-01-02 | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data
2023-01-03 | stop | stop | stop |  | stop | stop | 100% | 100% | 100% |  | 0% | 100% | stop | stop | stop | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | stop | stop
2023-01-04 | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data
2023-01-05 | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data
2023-01-06 | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data
2023-01-07 | stop | stop | stop |  | stop | stop | 100% | 100% | 100% |  | 0% | 100% | stop | stop | stop | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | stop | stop
2023-01-08 | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data
2023-01-09 | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data
2023-01-10 | stop | stop | stop |  | stop | stop | 100% | 100% | 100% |  | 100% | 100% | stop | stop | stop | stop | stop | stop | stop | stop |  | stop | stop | stop | stop | stop |  | stop | stop
2023-01-11 | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data
2023-01-12 | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data
2023-01-13 | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data
2023-01-14 | stop | stop | stop |  | stop | stop | 100% | 100% | 100% |  | 0% | 100% | no data | no data | no data | no data | no data | stop | stop | stop |  | stop | stop | stop | stop | stop |  | stop | stop
2023-01-15 | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data
2023-01-16 | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data
2023-01-17 | stop | stop | stop |  | stop | stop | 100% | 0% | 100% |  | 0% | 100% | no data | no data | no data | no data | no data | stop | stop | stop |  | stop | stop | stop | stop | stop |  | stop | stop
2023-01-18 | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data
2023-01-19 | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data
2023-01-20 | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data
2023-01-21 | stop | stop | stop |  | stop | stop | 100% | 100% | 100% |  | 0% | 100% | no data | no data | no data | no data | no data | stop | stop | stop |  | stop | stop | stop | stop | stop |  | stop | stop
2023-01-22 | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data
2023-01-23 | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data
2023-01-24 | stop | stop | stop |  | stop | stop | 100% | 100% | 100% |  | 0% | 100% | no data | no data | no data | no data | no data | stop | stop | stop |  | stop | stop | stop | stop | stop |  | stop | stop
2023-01-25 | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data
2023-01-26 | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data
2023-01-27 | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data
2023-01-28 | stop | stop | stop |  | stop | stop | 100% | 100% | 100% |  | 0% | 100% | no data | no data | no data | no data | no data | stop | stop | stop |  | stop | stop | stop | stop | stop |  | stop | stop
2023-01-29 | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data
2023-01-30 | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data
2023-01-31 | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data | no data | no data | no data | no data | no data |  | no data | no data | no data | no data | no data |  | no data | no data
CONFORMANCE | [6 empty] | 100% | 87.5% | 100% |  | 12.5% | 100%
OVERALL VALUE
Date
2023-01-01
2023-01-02
2023-01-03
2023-01-04
2023-01-05
2023-01-06
2023-01-07
2023-01-08
2023-01-09
2023-01-10
2023-01-11
2023-01-12
2023-01-13
2023-01-14
2023-01-15
2023-01-16
2023-01-17
2023-01-18
2023-01-19
2023-01-20
2023-01-21
2023-01-22
2023-01-23
2023-01-24
2023-01-25
2023-01-26
2023-01-27
2023-01-28
2023-01-29
2023-01-30
2023-01-31
CONFORMANCE
2023-01-01
2023-01-02
2023-01-03
2023-01-04
2023-01-05
2023-01-06
2023-01-07
2023-01-08
2023-01-09
2023-01-10
2023-01-11
2023-01-12
2023-01-13
2023-01-14
2023-01-15
2023-01-16
2023-01-17
2023-01-18
2023-01-19
2023-01-20
2023-01-21
2023-01-22
2023-01-23
2023-01-24
2023-01-25
2023-01-26
2023-01-27
2023-01-28
2023-01-29
2023-01-30
2023-01-31
Formulas:
DATE = '[2]RO & MIXBED'!A8

## TOTAL HARDNESS (hidden)
| 1 |  | 2 | 3 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |  |  |  | 6 | 7 | 8 | 9 | 6 | 7 | 8 | 9 | 9 | 9 | 9 | 10 | 11 | 12 |  | 13 | 14 | 15 | 16 | 17 | 18 | 19
| Demin Tank 2000 MT | Demin Tank BWRO | BUFFER DEMIN | RO Tank 200 | RO Tank 600 | Mixbed #2A | Mixbed #2B | Mixbed #1A | Mixbed #1B | Mixbed #3A | Mixbed #3B | Mixbed #4 | Mixbed #5A | Mixbed #5B | Mixbed Dyn 4 | Dyn #1 | Dyn #2 | Dyn #4 | Permeate #1A | Permeate #1B | Permeate #2 | Permeate #3A | Permeate #3B | Permeate #4A | Permeate #4B | BFW PP#1 | BFW PP32 | BFW PP#3 | BFW CFBC | TANK 200 | BFW HP Coal | BFW HP Gas | BFW TOH | BFW OMNICHAL | BFW GT#1 | BFW GT#2
Parameter | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3) | (ppm CaCO3)
| Trace | Trace | Trace | Trace | Trace | Trace | Trace | Trace | Trace | Trace | Trace | Trace | Trace | Trace | Trace | Trace | Trace | Trace | Trace | Trace | Trace | Trace | Trace | Trace | Trace | 0.1; Max | 0.1; Max | 0.1; Max | 0.1; Max | Trace | 0.1; Max | 0.1; Max | 0.3; Max | 0.3; Max | 0.3; Max | 0.3; Max
1
2026-09-01
2026-09-02
2026-09-03
2026-09-04
2026-09-05
2026-09-06
2026-09-07
2026-09-08
2026-09-09
2026-09-10
2026-09-11
2026-09-12
2026-09-13
2026-09-14
2026-09-15
2026-09-16
2026-09-17
2026-09-18
2026-09-19
2026-09-20
2026-09-21
2026-09-22
2026-09-23
2026-09-24
2026-09-25
2026-09-26
2026-09-27
2026-09-28
2026-09-29
2026-09-30
2026-10-01